## Interface
Motor Blower
Static
Attachments
First Pre-Filter
Second Pre-Filter
First Main Filter
Second Main Filter

## Equations (hidden)
Motor Blower Curves
1.5 HP Curves
1.5 HP Low Static- N/A
1.5 HP Medium Static
1015 RPM | y = -0.000000000046767x3 + 0.000000181036063x2 - 0.000318901654677x + 1.496158114271400
1375 RPM | y = 0.000000000007186x3 - 0.000000006615077x2 - 0.000143057536990x + 2.420779291671950
1.5 HP High Static
1250 RPM | y = -0.000000000058650x3 + 0.000000202924904x2 - 0.000305618732789x + 2.023930179143210
1600 RPM | y = 0.000000000178797x3 - 0.000000457156441x2 + 0.000173812749743x + 3.167311146223180
2 HP Curves
2 HP Low Static
1150 RPM | y = -0.000000000076364x3 + 0.000000267403042x2 - 0.000421744847700x + 2.051753852096680
1375 RPM | y = -0.000000000077985x3 + 0.000000321691988x2 - 0.000502880582786x + 2.664055977857320
2 HP Medium Static
1325 RPM | y = -0.000000000077985x3 + 0.000000321691988x2 - 0.000502880582786x + 2.604055977857310
1575 RPM | y = -0.000000000068380x3 + 0.000000365180703x2 - 0.000703827171737x + 3.452308423843610
2 HP High Static
1550 RPM | y = -0.000000000074621x3 + 0.000000388787836x2 - 0.000728747335796x + 3.358949832070300
1850 RPM | y = -0.000000000135237x3 + 0.000000596403533x2 - 0.001088269982483x + 4.752399971342040
3 HP Curves
3 HP Low Static
1150 RPM | y = -0.000000000076364x3 + 0.000000267403042x2 - 0.000421744847700x + 2.051753852096680
1375 RPM | y = -0.000000000077985x3 + 0.000000321691988x2 - 0.000502880582786x + 2.664055977857320
3 HP Medium Static
1325 RPM | y = -0.000000000077985x3 + 0.000000321691988x2 - 0.000502880582786x + 2.604055977857310
1575 RPM | y = -0.000000000068380x3 + 0.000000365180703x2 - 0.000703827171737x + 3.452308423843610
3 HP High Static
1550 RPM | y = -0.000000000074621x3 + 0.000000388787836x2 - 0.000728747335796x + 3.358949832070300
1850 RPM | y = -0.000000000135237x3 + 0.000000596403533x2 - 0.001088269982483x + 4.752399971342040
3 HP Explosion Proof & 575 Volt Curves
3 HP Low Static
1200 RPM | y = -0.000000000066438x3 + 0.000000237041193x2 - 0.000400817267706x + 2.147213576910140
1550 RPM | y = -0.000000000089053x3 + 0.000000444622167x2 - 0.000788887424525x + 3.375207473843640
3 HP High Static
1500 RPM | y = -0.000000000058394x3 + 0.000000294404781x2 - 0.000548432475317x + 3.151649132877280
1950 RPM | y = -0.000000000207149x3 + 0.000000816099221x2 - 0.001263728445811x + 5.090499248712250
Filter Curves
2" Pleat | y = 0.000000063544964x2 + 0.000173077018203x
4" Pleat | y = 0.000000066958830x2 + 0.000052688362741x
2" Mesh | y = 0.000000009949530x2 + 0.000034048671408x
2" Baffle | y = 0.000000000160356x3 - 0.000000060965061x2 + 0.000309491068520x
2" Maxi Grid | y = 0.000000009949530x2 + 0.000034048671408x
Wrap Around Pre-Filter | y = 0.000000009949530x2 + 0.000034048671408x
Washable | y = 0.000000097876391x2 + 0.000067654027678x
55% Bag | y = 0.000000066958830x2 + 0.000052688362741x
95% Bag | y = 0.000000049942838x2 + 0.000247119253373x
95% Short Bag | y = 0.000000067777197x2 + 0.000373005380130x
95% Oil Bag | y = 0.000000063544964x2 + 0.000173077018203x
95% Short Oil | y = 0.000000036115289x2 + 0.000509030332800x
95% HEPA | y = 0.000000067777197x2 + 0.000373005380130x
99% HEPA | y = 0.000000000304519x3 - 0.000000804647078x2 + 0.001281517505193x
RCM30 | y = 0.000000539256544x2 + 0.000082190446123x
Cheveron | y = 0.000000000037810x3 - 0.000000093858399x2 + 0.000181912903345x

## Filters (hidden)
Filter Resistance Data
Corrected Filter Resistance Curve Data
CFM | 2" pleat | 4" pleat | 2" mesh | 2" baffle | 2" maxi grid | washable | 55% bag | 95% bag | 95% short bag | 95% oil | 95% short oil | 95% HEPA | 99% HEPA | RCM30 | Cheveron
200 | 0.075 | 0.005 | 0.005 | 0.075 | 0.005 | 0.055 | 0.005 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.145 | 0.105 | 0.025
400 | 0.09 | 0.01 | 0.01 | 0.09 | 0.01 | 0.07 | 0.01 | 0.09 | 0.14 | 0.09 | 0.14 | 0.14 | 0.29 | 0.19 | 0.03
600 | 0.115 | 0.075 | 0.025 | 0.115 | 0.025 | 0.085 | 0.075 | 0.115 | 0.235 | 0.115 | 0.235 | 0.235 | 0.435 | 0.305 | 0.075
800 | 0.18 | 0.09 | 0.04 | 0.23 | 0.04 | 0.12 | 0.09 | 0.18 | 0.33 | 0.18 | 0.33 | 0.33 | 0.63 | 0.47 | 0.09
1000 | 0.225 | 0.125 | 0.055 | 0.375 | 0.055 | 0.155 | 0.125 | 0.225 | 0.425 | 0.225 | 0.425 | 0.425 | 0.805 | 0.625 | 0.105
1200 | 0.3 | 0.19 | 0.07 | 0.595 | 0.07 | 0.21 | 0.19 | 0.3 | 0.55 | 0.3 | 0.55 | 0.55 | 0.97 | 0.85 | 0.12
1400 | 0.38 | 0.2 | 0.07 | 0.79 | 0.07 | 0.23 | 0.2 | 0.38 | 0.66 | 0.38 | 0.66 | 0.66 | 1.16 | 1.13 | 0.13
1600 | 0.43 | 0.26 | 0.07 | 1.15 | 0.07 | 0.31 | 0.26 | 0.43 | 0.8 | 0.43 | 0.8 | 0.8 | 1.35 | 1.4 | 0.17
1800 | 0.5 | 0.3 | 0.08 | 1.34 | 0.08 | 0.49 | 0.3 | 0.5 | 0.89 | 0.5 | 0.89 | 0.89 | 1.54 | 1.82 | 0.21
2000 | 0.61 | 0.37 | 0.11 | 1.68 | 0.11 | 0.53 | 0.37 | 0.61 | 1.03 | 0.61 | 1.03 | 1.03 | 1.76 | 2.26 | 0.25
2200 | 0.69 | 0.4 | 0.11 | 2.04 | 0.11 | 0.65 | 0.4 | 0.69 | 1.13 | 0.69 | 1.13 | 1.13 | 2.06 | 3.01 | 0.3
2400 | 0.79 | 0.51 | 0.14 | 2.54 | 0.14 | 0.74 | 0.51 | 0.79 | 1.29 | 0.79 | 1.29 | 1.29 | 2.57 | 3.29 | 0.37
2600 | 0.87 | 0.59 | 0.16 | 3.12 | 0.16 | 0.87 | 0.59 | 0.87 | 1.45 | 0.87 | 1.45 | 1.45 | 3.17 | 3.87 | 0.39
2800 | 1 | 0.71 | 0.17 | 3.85 | 0.17 | 0.95 | 0.71 | 1 | 1.55 | 1 | 1.55 | 1.55 | 3.95 | 4.45 | 0.5
3000 | 1.08 | 0.75 | 0.2 | 4.83 | 0.2 | 1.05 | 0.75 | 1.08 | 1.73 | 1.08 | 1.73 | 1.73 | 4.93 | 5.08 | 0.61
[11 empty] | 2" Pleat | y = 0.000000063544964x2 + 0.000173077018203x
[11 empty] | 4" Pleat | y = 0.000000066958830x2 + 0.000052688362741x
[11 empty] | 2" Mesh | y = 0.000000009949530x2 + 0.000034048671408x
[11 empty] | 2" Baffle | y = 0.000000000160356x3 - 0.000000060965061x2 + 0.000309491068520x
[11 empty] | 2" Maxi Grid | y = 0.000000009949530x2 + 0.000034048671408x
[11 empty] | Washable | y = 0.000000097876391x2 + 0.000067654027678x
[11 empty] | 55% Bag | y = 0.000000066958830x2 + 0.000052688362741x
[11 empty] | 95% Bag | y = 0.000000049942838x2 + 0.000247119253373x
[11 empty] | 95% Short Bag | y = 0.000000067777197x2 + 0.000373005380130x
[11 empty] | 95% Oil Bag | y = 0.000000063544964x2 + 0.000173077018203x
[11 empty] | 95% Short Oil | y = 0.000000036115289x2 + 0.000509030332800x
[11 empty] | 95% HEPA | y = 0.000000067777197x2 + 0.000373005380130x
[11 empty] | 99% HEPA | y = 0.000000000304519x3 - 0.000000804647078x2 + 0.001281517505193x
[11 empty] | RCM30 | y = 0.000000539256544x2 + 0.000082190446123x
[11 empty] | Cheveron | y = 0.000000000037810x3 - 0.000000093858399x2 + 0.000181912903345x

## Blowers (hidden)
Low Static 3HP Option
max. |  | min.
1375 rpm |  | 1150 rpm
cfm | s.p. | cfm | s.p.
300 | 2.55 | 300 | 1.96
400 | 2.5 | 400 | 1.93
500 | 2.48 | 500 | 1.88
800 | 2.42 | 800 | 1.85
1000 | 2.41 | 1000 | 1.8
1300 | 2.4 | 1300 | 1.78
1500 | 2.37 | 1500 | 1.76
1700 | 2.35 | 1700 | 1.75
2100 | 2.29 | 2100 | 1.65
2300 | 2.26 | 2300 | 1.58
2500 | 2.2 | 2500 | 1.5
2750 | 2.1 | 2750 | 1.3
3000 | 1.95 | 3000 | 1.1
3300 | 1.7 | 3300 | 0.82
|  | 3500 | 0.6
|  | 1150 RPM | y = -0.000000000076364x3 + 0.000000267403042x2 - 0.000421744847700x + 2.051753852096680
|  | 1375 RPM | y = -0.000000000077985x3 + 0.000000321691988x2 - 0.000502880582786x + 2.664055977857320
Med Static 3HP Option
max. |  | min.
1575 rpm |  | 1325 rpm
cfm | s.p. | cfm | s.p.
300 | 3.3 | 300 | 2.49
400 | 3.22 | 400 | 2.44
500 | 3.15 | 500 | 2.42
800 | 3.08 | 800 | 2.36
1000 | 3.05 | 1000 | 2.35
1300 | 3.02 | 1300 | 2.34
1500 | 3 | 1500 | 2.31
1700 | 2.97 | 1700 | 2.29
2100 | 2.95 | 2100 | 2.23
2300 | 2.92 | 2300 | 2.2
2500 | 2.9 | 2500 | 2.14
2700 | 2.88 | 2750 | 2.04
|  | 3000 | 1.89
|  | 3300 | 1.64
|  | 1325 RPM | y = -0.000000000077985x3 + 0.000000321691988x2 - 0.000502880582786x + 2.604055977857310
|  | 1575 RPM | y = -0.000000000068380x3 + 0.000000365180703x2 - 0.000703827171737x + 3.452308423843610
3 HP High Static
1850 RPM |  | 1550 RPM
CFM | S.P. | CFM | S.P.
300 | 4.5 | 300 | 3.2
400 | 4.4 | 400 | 3.12
500 | 4.3 | 500 | 3.05
800 | 4.2 | 800 | 2.98
1000 | 4.15 | 1000 | 2.95
1300 | 4.05 | 1300 | 2.92
1500 | 4 | 1500 | 2.9
1700 | 3.95 | 1700 | 2.87
2100 | 3.85 | 2100 | 2.85
|  | 2300 | 2.82
|  | 2500 | 2.8
|  | 2750 | 2.75
1850 RPM
y = -0.000000000135237x3 + 0.000000596403533x2 - 0.001088269982483x + 4.752399971342040
1550 RPM
y = -0.000000000074621x3 + 0.000000388787836x2 - 0.000728747335796x + 3.358949832070300
1.5 HP Medium Static
1375 RPM |  | 1015 RPM
CFM | S.P. | CFM | S.P.
300 | 2.38 | 300 | 1.4
400 | 2.36 | 400 | 1.39
500 | 2.35 | 500 | 1.38
800 | 2.3 | 800 | 1.36
1000 | 2.28 | 1000 | 1.34
1300 | 2.25 | 1300 | 1.28
1500 | 2.21 | 1500 | 1.24
1700 | 2.19 | 1700 | 1.21
2100 | 2.16 | 2100 | 1.19
2200 | 2.15 | 2200 | 1.18
|  | 2500 | 1.125
|  | 2600 | 1.1
|  | 2750 | 1
|  | 3000 | 0.89
1375 RPM
y = 0.000000000007186x3 - 0.000000006615077x2 - 0.000143057536990x + 2.420779291671950
1015 RPM
y = -0.000000000046767x3 + 0.000000181036063x2 - 0.000318901654677x + 1.496158114271400
1.5 HP High Static
1600 RPM |  | 1250 RPM
CFM | S.P. | CFM | S.P.
300 | 3.18 | 300 | 1.95
400 | 3.175 | 400 | 1.93
500 | 3.17 | 500 | 1.91
800 | 3.1 | 800 | 1.88
1000 | 3.06 | 1000 | 1.87
1300 | 3.02 | 1300 | 1.85
1500 | 3 | 1500 | 1.81
|  | 1700 | 1.8
|  | 2100 | 1.72
|  | 2300 | 1.7
|  | 2500 | 1.63
|  | 2600 | 1.55
|  | 1600 RPM | y = 0.000000000178797x3 - 0.000000457156441x2 + 0.000173812749743x + 3.167311146223180
|  | 1250 RPM | y = -0.000000000058650x3 + 0.000000202924904x2 - 0.000305618732789x + 2.023930179143210
Low Static 3HP Exploded & 575V Option
max. |  | min.
1200 rpm |  | 1550 rpm
cfm | s.p. | cfm | s.p.
300 | 2.05 | 300 | 3.2
400 | 2.02 | 400 | 3.12
500 | 2 | 500 | 3.05
800 | 1.94 | 800 | 2.98
1000 | 1.9 | 1000 | 2.95
1300 | 1.9 | 1300 | 2.92
1500 | 1.87 | 1500 | 2.9
1700 | 1.8 | 1700 | 2.87
2100 | 1.72 | 2100 | 2.85
2300 | 1.69 | 2300 | 2.82
2500 | 1.6 | 2500 | 2.8
2750 | 1.5
3000 | 1.2
3300 | 1.05
|  | 1200 RPM | y = -0.000000000066438x3 + 0.000000237041193x2 - 0.000400817267706x + 2.147213576910140
|  | 1550 RPM | y = -0.000000000089053x3 + 0.000000444622167x2 - 0.000788887424525x + 3.375207473843640
High Static 3HP E.P. or 575 Volt Option
max. |  | min.
1950 rpm |  | 1500 rpm
cfm | s.p. | cfm | s.p.
300 | 4.8 | 300 | 3.05
400 | 4.7 | 400 | 2.96
500 | 4.6 | 500 | 2.9
800 | 4.5 | 800 | 2.88
1000 | 4.46 | 1000 | 2.85
1300 | 4.38 | 1300 | 2.81
1500 | 4.31 | 1500 | 2.8
1700 | 4.28 | 1700 | 2.79
1950 | 4.2 | 2100 | 2.75
|  | 2300 | 2.72
|  | 2500 | 2.71
|  | 2600 | 2.7
|  | 1500 RPM | y = -0.000000000058394x3 + 0.000000294404781x2 - 0.000548432475317x + 3.151649132877280
|  | 1950 RPM | y = -0.000000000207149x3 + 0.000000816099221x2 - 0.001263728445811x + 5.090499248712250

## Options (hidden)
Motor
1.5 HP
2 HP
3 HP
3 HP (E.P. or 575V)
Static
Low
Medium
High
Attachments
None
Wrap Around Pre-Filter
3 - 8" Collars
2 - 10" Collars
1 - 16" Collar
First Pre-Filter
None
Washable
2" Pleated
2" Alumninum Mesh
2" Baffle Impinger
4" Pleated
Second Pre-Filter
None
Washable
2" Pleated
2" Alumninum Mesh
2" Baffle Impinger
First Main Filter
None
12" 95% HEPA
12" 99% HEPA
Refillable Module
55% Long Bag
95% Long Bag
95% Short Bag
Second Main Filter
None
12" 95% HEPA
12" 99% HEPA
Refillable Module

## Curve Cut-Off (hidden)
1.5 HP Cut-Offs
Low Static |  | Medium Static |  | High Static
0 RPM | 0 RPM | 1375 RPM | 1015 RPM | 1600 RPM | 1250 RPM
0 | 0 | 2200 | 3000 | 1400 | 2600
2 HP Cut-Offs
Low Static |  | Medium Static |  | High Static
1375 RPM | 1150 RPM | 1575 RPM | 1325 RPM | 1850 RPM | 1550 RPM
2800 | 3000 | 2400 | 2800 | 1800 | 2600
3 HP Cut-Offs
Low Static |  | Medium Static |  | High Static
1375 RPM | 1150 RPM | 1575 RPM | 1325 RPM | 1850 RPM | 1550 RPM
3200 | 3400 | 2600 | 3200 | 2100 | 2800
3 HP Explosion Proof or 575 Volt Cut-Offs
Low Static |  | Medium Static |  | High Static
1200 RPM | 1550 RPM | 0 RPM | 0 RPM | 1500 RPM | 1950 RPM
3400 | 2400 | 0 | 0 | 2600 | 2000

## Data (hidden)
Motor |  |  |  | Curve Cut-Off CFM for All Motors at Various Static Ratings
Choose a Motor |  | 3 |  | High RPM Curve Cut-Off | [5 empty] | Low RPM Curve Cut-Off
|  |  |  | 1.5 HP | 2 HP | 3 HP | 3 HP EP/575V | Sum |  | 1.5 HP | 2 HP | 3 HP | 3 HP EP/575V | Sum
1 = 1.5 HP |  |  |  | 0 | 0 | 1 | 0 | 1 |  | 0 | 0 | 1 | 0 | 1
2 = 2 HP |  | Connector Line (End Connector) |  | 0 | 0 | 201 | 0 | 201 |  | 0 | 0 | 201 | 0 | 201
3 = 3 HP |  | 2201 | 3.8044 | 0 | 0 | 401 | 0 | 401 |  | 0 | 0 | 401 | 0 | 401
4 = 3 HP (E.P) |  | 2801 | 2.7282 | 0 | 0 | 601 | 0 | 601 |  | 0 | 0 | 601 | 0 | 601
|  |  |  | 0 | 0 | 801 | 0 | 801 |  | 0 | 0 | 801 | 0 | 801
|  |  |  | 0 | 0 | 1001 | 0 | 1001 |  | 0 | 0 | 1001 | 0 | 1001
|  |  |  | 0 | 0 | 1201 | 0 | 1201 |  | 0 | 0 | 1201 | 0 | 1201
|  |  |  | 0 | 0 | 1401 | 0 | 1401 |  | 0 | 0 | 1401 | 0 | 1401
|  |  |  | 0 | 0 | 1601 | 0 | 1601 |  | 0 | 0 | 1601 | 0 | 1601
|  |  |  | 0 | 0 | 1801 | 0 | 1801 |  | 0 | 0 | 1801 | 0 | 1801
|  |  |  | 0 | 0 | 2001 | 0 | 2001 |  | 0 | 0 | 2001 | 0 | 2001
|  |  |  | 0 | 0 | 2201 | 0 | 2201 |  | 0 | 0 | 2201 | 0 | 2201
|  |  |  | 0 | 0 | 2201 | 0 | 2201 |  | 0 | 0 | 2401 | 0 | 2401
|  |  |  | 0 | 0 | 2201 | 0 | 2201 |  | 0 | 0 | 2601 | 0 | 2601
|  |  |  | 0 | 0 | 2201 | 0 | 2201 |  | 0 | 0 | 2801 | 0 | 2801
|  |  |  | 0 | 0 | 2201 | 0 | 2201 |  | 0 | 0 | 2801 | 0 | 2801
|  |  |  | 0 | 0 | 2201 | 0 | 2201 |  | 0 | 0 | 2801 | 0 | 2801
|  |  |  | 0 | 0 | 2201 | 0 | 2201 |  | 0 | 0 | 2801 | 0 | 2801
|  |  |  | 0 | 0 | 2201 | 0 | 2201 |  | 0 | 0 | 2801 | 0 | 2801
|  |  |  | 0 | 0 | 2201 | 0 | 2201 |  | 0 | 0 | 2801 | 0 | 2801
|  |  |  | 0 | 0 | 2201 | 0 | 2201 |  | 0 | 0 | 2801 | 0 | 2801
High / Low RPM Blower Curve Generation
Static |  |  |  |  | High RPM | [5 empty] | Low RPM
Choose a Static |  | 3 |  |  | 1.5 HP | 2 HP | 3 HP | 3 HP EP | Total (Sum) |  | 1.5 HP | 2 HP | 3 HP | 3 HP EP | Total (Sum)
|  | (High RPM Curve) | (Low RPM Curve) |  | Max | Max | Max | Max | Max |  | Min | Min | Min | Min | Min
1 = Low (N/A 1.5HP) |  | 1 | 1 |  | 0 | 0 | 4.7513 | 0 | 4.7513 |  | 0 | 0 | 3.3582 | 0 | 3.3582
2 = Medium |  | 201 | 201 |  | 0 | 0 | 4.5567 | 0 | 4.5567 |  | 0 | 0 | 3.2276 | 0 | 3.2276
3 = High |  | 401 | 401 |  | 0 | 0 | 4.4032 | 0 | 4.4032 |  | 0 | 0 | 3.1244 | 0 | 3.1244
|  | 601 | 601 |  | 0 | 0 | 4.2844 | 0 | 4.2844 |  | 0 | 0 | 3.0452 | 0 | 3.0452
|  | 801 | 801 |  | 0 | 0 | 4.1938 | 0 | 4.1938 |  | 0 | 0 | 2.9863 | 0 | 2.9863
|  | 1001 | 1001 |  | 0 | 0 | 4.125 | 0 | 4.125 |  | 0 | 0 | 2.9442 | 0 | 2.9442
|  | 1201 | 1201 |  | 0 | 0 | 4.0714 | 0 | 4.0714 |  | 0 | 0 | 2.9152 | 0 | 2.9152
|  | 1401 | 1401 |  | 0 | 0 | 4.0265 | 0 | 4.0265 |  | 0 | 0 | 2.8959 | 0 | 2.8959
|  | 1601 | 1601 |  | 0 | 0 | 3.9838 | 0 | 3.9838 |  | 0 | 0 | 2.8825 | 0 | 2.8825
|  | 1801 | 1801 |  | 0 | 0 | 3.9369 | 0 | 3.9369 |  | 0 | 0 | 2.8716 | 0 | 2.8716
|  | 2001 | 2001 |  | 0 | 0 | 3.8793 | 0 | 3.8793 |  | 0 | 0 | 2.8596 | 0 | 2.8596
|  | 2201 | 2201 |  | 0 | 0 | 3.8044 | 0 | 3.8044 |  | 0 | 0 | 2.8428 | 0 | 2.8428
|  | 2201 | 2401 |  | 0 | 0 | 3.8044 | 0 | 3.8044 |  | 0 | 0 | 2.8177 | 0 | 2.8177
|  | 2201 | 2601 |  | 0 | 0 | 3.8044 | 0 | 3.8044 |  | 0 | 0 | 2.7807 | 0 | 2.7807
|  | 2201 | 2801 |  | 0 | 0 | 3.8044 | 0 | 3.8044 |  | 0 | 0 | 2.7282 | 0 | 2.7282
|  | 2201 | 2801 |  | 0 | 0 | 3.8044 | 0 | 3.8044 |  | 0 | 0 | 2.7282 | 0 | 2.7282
|  | 2201 | 2801 |  | 0 | 0 | 3.8044 | 0 | 3.8044 |  | 0 | 0 | 2.7282 | 0 | 2.7282
|  | 2201 | 2801 |  | 0 | 0 | 3.8044 | 0 | 3.8044 |  | 0 | 0 | 2.7282 | 0 | 2.7282
|  | 2201 | 2801 |  | 0 | 0 | 3.8044 | 0 | 3.8044 |  | 0 | 0 | 2.7282 | 0 | 2.7282
|  | 2201 | 2801 |  | 0 | 0 | 3.8044 | 0 | 3.8044 |  | 0 | 0 | 2.7282 | 0 | 2.7282
|  | 2201 | 2801 |  | 0 | 0 | 3.8044 | 0 | 3.8044 |  | 0 | 0 | 2.7282 | 0 | 2.7282
Attachment (Inlet)
Attachment Arrangement |  | 2
None | 1 | (High RPM Curve) | (Low RPM Curve) | High RPM | Low RPM |  | High RPM | Low RPM
Wrap Around Pre-Filter | 2 |  |  | S.P. Drop | S.P. Drop |  | Curve | Curve
3 - 8" Collars | 3 | 1 | 1 | 3.4059e-05 | 3.4059e-05 |  | 4.7513 | 3.3582
2 - 10" Collars | 4 | 201 | 201 | 0.0072458 | 0.0072458 |  | 4.5494 | 3.2203
1 - 16" Collars | 5 | 401 | 401 | 0.015253 | 0.015253 |  | 4.3879 | 3.1092
|  | 601 | 601 | 0.024057 | 0.024057 |  | 4.2604 | 3.0211
|  | 801 | 801 | 0.033657 | 0.033657 |  | 4.1602 | 2.9527
Entry Loss Factor (per VP) |  | 1001 | 1001 | 0.044052 | 0.044052 |  | 4.0809 | 2.9001
1 |  | 1201 | 1201 | 0.055244 | 0.055244 |  | 4.0161 | 2.86
|  | 1401 | 1401 | 0.067231 | 0.067231 |  | 3.9592 | 2.8287
Area of 3 - 8" Collars |  | 1601 | 1601 | 0.080015 | 0.080015 |  | 3.9038 | 2.8025
1.1373 |  | 1801 | 1801 | 0.093594 | 0.093594 |  | 3.8433 | 2.778
|  | 2001 | 2001 | 0.10797 | 0.10797 |  | 3.7713 | 2.7516
Area of 2 - 10" Collars |  | 2201 | 2201 | 0.12314 | 0.12314 |  | 3.6812 | 2.7196
1.0908 |  | 2201 | 2401 | 0.12314 | 0.13911 |  | 3.6812 | 2.6786
|  | 2201 | 2601 | 0.12314 | 0.15587 |  | 3.6812 | 2.6248
Area of 1 - 16" Collars |  | 2201 | 2801 | 0.12314 | 0.17343 |  | 3.6812 | 2.5547
1.3963 |  | 2201 | 2801 | 0.12314 | 0.17343 |  | 3.6812 | 2.5547
|  | 2201 | 2801 | 0.12314 | 0.17343 |  | 3.6812 | 2.5547
|  | 2201 | 2801 | 0.12314 | 0.17343 |  | 3.6812 | 2.5547
|  | 2201 | 2801 | 0.12314 | 0.17343 |  | 3.6812 | 2.5547
|  | 2201 | 2801 | 0.12314 | 0.17343 |  | 3.6812 | 2.5547
|  | 2201 | 2801 | 0.12314 | 0.17343 |  | 3.6812 | 2.5547
First Pre-Filter |  | 2 |  | High RPM | Low RPM |  | High RPM | Low RPM
|  | (High RPM Curve) | (Low RPM Curve) | S.P. Drop | S.P. Drop |  | Curve | Curve
None | 1 | 1 | 1 | 6.7752e-05 | 6.7752e-05 |  | 4.7512 | 3.3581
Washable | 2 | 201 | 201 | 0.017553 | 0.017553 |  | 4.5319 | 3.2028
2" Pleated | 3 | 401 | 401 | 0.042868 | 0.042868 |  | 4.3451 | 3.0663
2" Alumninum Mesh | 4 | 601 | 601 | 0.076013 | 0.076013 |  | 4.1843 | 2.9451
2" Baffle Impinger | 5 | 801 | 801 | 0.11699 | 0.11699 |  | 4.0432 | 2.8357
4" Pleated | 6 | 1001 | 1001 | 0.16579 | 0.16579 |  | 3.9151 | 2.7343
|  | 1201 | 1201 | 0.22243 | 0.22243 |  | 3.7937 | 2.6376
|  | 1401 | 1401 | 0.2869 | 0.2869 |  | 3.6723 | 2.5418
|  | 1601 | 1601 | 0.35919 | 0.35919 |  | 3.5446 | 2.4433
Filter Divider |  | 1801 | 1801 | 0.43932 | 0.43932 |  | 3.404 | 2.3387
1 |  | 2001 | 2001 | 0.52727 | 0.52727 |  | 3.244 | 2.2243
|  | 2201 | 2201 | 0.62306 | 0.62306 |  | 3.0582 | 2.0966
|  | 2201 | 2401 | 0.62306 | 0.72668 |  | 3.0582 | 1.9519
|  | 2201 | 2601 | 0.62306 | 0.83812 |  | 3.0582 | 1.7867
|  | 2201 | 2801 | 0.62306 | 0.9574 |  | 3.0582 | 1.5973
|  | 2201 | 2801 | 0.62306 | 0.9574 |  | 3.0582 | 1.5973
|  | 2201 | 2801 | 0.62306 | 0.9574 |  | 3.0582 | 1.5973
|  | 2201 | 2801 | 0.62306 | 0.9574 |  | 3.0582 | 1.5973
|  | 2201 | 2801 | 0.62306 | 0.9574 |  | 3.0582 | 1.5973
|  | 2201 | 2801 | 0.62306 | 0.9574 |  | 3.0582 | 1.5973
|  | 2201 | 2801 | 0.62306 | 0.9574 |  | 3.0582 | 1.5973
Second Pre-Filter |  | 4
|  |  |  | High RPM | Low RPM |  | High RPM | Low RPM
|  | (High RPM Curve) | (Low RPM Curve) | S.P. Drop | S.P. Drop |  | Curve | Curve
None | 1 | 1 | 1 | 3.4059e-05 | 3.4059e-05 |  | 4.7512 | 3.3581
Washable | 2 | 201 | 201 | 0.0072458 | 0.0072458 |  | 4.5246 | 3.1955
2" Pleated | 3 | 401 | 401 | 0.015253 | 0.015253 |  | 4.3298 | 3.0511
2" Alumninum Mesh | 4 | 601 | 601 | 0.024057 | 0.024057 |  | 4.1603 | 2.9211
2" Baffle Impinger | 5 | 801 | 801 | 0.033657 | 0.033657 |  | 4.0095 | 2.802
|  | 1001 | 1001 | 0.044052 | 0.044052 |  | 3.8711 | 2.6903
|  | 1201 | 1201 | 0.055244 | 0.055244 |  | 3.7384 | 2.5823
|  | 1401 | 1401 | 0.067231 | 0.067231 |  | 3.6051 | 2.4745
Filter Divider |  | 1601 | 1601 | 0.080015 | 0.080015 |  | 3.4646 | 2.3633
1 |  | 1801 | 1801 | 0.093594 | 0.093594 |  | 3.3104 | 2.2451
|  | 2001 | 2001 | 0.10797 | 0.10797 |  | 3.136 | 2.1164
|  | 2201 | 2201 | 0.12314 | 0.12314 |  | 2.935 | 1.9734
|  | 2201 | 2401 | 0.12314 | 0.13911 |  | 2.935 | 1.8128
|  | 2201 | 2601 | 0.12314 | 0.15587 |  | 2.935 | 1.6308
|  | 2201 | 2801 | 0.12314 | 0.17343 |  | 2.935 | 1.4239
|  | 2201 | 2801 | 0.12314 | 0.17343 |  | 2.935 | 1.4239
|  | 2201 | 2801 | 0.12314 | 0.17343 |  | 2.935 | 1.4239
|  | 2201 | 2801 | 0.12314 | 0.17343 |  | 2.935 | 1.4239
|  | 2201 | 2801 | 0.12314 | 0.17343 |  | 2.935 | 1.4239
|  | 2201 | 2801 | 0.12314 | 0.17343 |  | 2.935 | 1.4239
|  | 2201 | 2801 | 0.12314 | 0.17343 |  | 2.935 | 1.4239
First Main Filter |  | 5
|  |  |  | High RPM | Low RPM |  | High RPM | Low RPM
|  | (High RPM Curve) | (Low RPM Curve) | S.P. Drop | S.P. Drop |  | Curve | Curve
None | 1 | 1 | 1 | 5.2755e-05 | 5.2755e-05 |  | 4.7511 | 3.358
12" 95% HEPA | 2 | 201 | 201 | 0.013296 | 0.013296 |  | 4.5113 | 3.1822
12" 99% HEPA | 3 | 401 | 401 | 0.031895 | 0.031895 |  | 4.2979 | 3.0192
Refillable Module | 4 | 601 | 601 | 0.055851 | 0.055851 |  | 4.1044 | 2.8652
55% Long Bag | 5 | 801 | 801 | 0.085164 | 0.085164 |  | 3.9244 | 2.7169
95% Long Bag | 6 | 1001 | 1001 | 0.11983 | 0.11983 |  | 3.7513 | 2.5705
95% Short Bag | 7 | 1201 | 1201 | 0.15986 | 0.15986 |  | 3.5786 | 2.4225
|  | 1401 | 1401 | 0.20524 | 0.20524 |  | 3.3999 | 2.2693
|  | 1601 | 1601 | 0.25598 | 0.25598 |  | 3.2086 | 2.1073
Filter Divider |  | 1801 | 1801 | 0.31208 | 0.31208 |  | 2.9983 | 1.933
1 |  | 2001 | 2001 | 0.37353 | 0.37353 |  | 2.7625 | 1.7428
|  | 2201 | 2201 | 0.44034 | 0.44034 |  | 2.4947 | 1.5331
|  | 2201 | 2401 | 0.44034 | 0.51251 |  | 2.4947 | 1.3003
|  | 2201 | 2601 | 0.44034 | 0.59003 |  | 2.4947 | 1.0408
|  | 2201 | 2801 | 0.44034 | 0.67291 |  | 2.4947 | 0.751
|  | 2201 | 2801 | 0.44034 | 0.67291 |  | 2.4947 | 0.751
|  | 2201 | 2801 | 0.44034 | 0.67291 |  | 2.4947 | 0.751
|  | 2201 | 2801 | 0.44034 | 0.67291 |  | 2.4947 | 0.751
|  | 2201 | 2801 | 0.44034 | 0.67291 |  | 2.4947 | 0.751
|  | 2201 | 2801 | 0.44034 | 0.67291 |  | 2.4947 | 0.751
|  | 2201 | 2801 | 0.44034 | 0.67291 |  | 2.4947 | 0.751
Second Main Filter |  | 1
|  |  |  | High RPM | Low RPM |  | High RPM | Low RPM
|  | (High RPM Curve) | (Low RPM Curve) | S.P. Drop | S.P. Drop |  | Curve | Curve
None | 1 | 1 | 1 | 0 | 0 |  | 4.7511 | 3.358
12" 95% HEPA | 2 | 201 | 201 | 0 | 0 |  | 4.5113 | 3.1822
12" 99% HEPA | 3 | 401 | 401 | 0 | 0 |  | 4.2979 | 3.0192
Refillable Module | 4 | 601 | 601 | 0 | 0 |  | 4.1044 | 2.8652
|  | 801 | 801 | 0 | 0 |  | 3.9244 | 2.7169
|  | 1001 | 1001 | 0 | 0 |  | 3.7513 | 2.5705
|  | 1201 | 1201 | 0 | 0 |  | 3.5786 | 2.4225
Filter Divider |  | 1401 | 1401 | 0 | 0 |  | 3.3999 | 2.2693
1 |  | 1601 | 1601 | 0 | 0 |  | 3.2086 | 2.1073
|  | 1801 | 1801 | 0 | 0 |  | 2.9983 | 1.933
|  | 2001 | 2001 | 0 | 0 |  | 2.7625 | 1.7428
|  | 2201 | 2201 | 0 | 0 |  | 2.4947 | 1.5331
|  | 2201 | 2401 | 0 | 0 |  | 2.4947 | 1.3003
|  | 2201 | 2601 | 0 | 0 |  | 2.4947 | 1.0408
|  | 2201 | 2801 | 0 | 0 |  | 2.4947 | 0.751
|  | 2201 | 2801 | 0 | 0 |  | 2.4947 | 0.751
|  | 2201 | 2801 | 0 | 0 |  | 2.4947 | 0.751
|  | 2201 | 2801 | 0 | 0 |  | 2.4947 | 0.751
|  | 2201 | 2801 | 0 | 0 |  | 2.4947 | 0.751
|  | 2201 | 2801 | 0 | 0 |  | 2.4947 | 0.751
|  | 2201 | 2801 | 0 | 0 |  | 2.4947 | 0.751
Connector Line
|  |  |  | 2201 | 2.4947
|  |  |  | 2801 | 0.751
Note on A1: Jerold: The motor Option is used to limit the CFM. This is due to Over Current Limitations.
Note on A29: Jerold: The Static Option is where the curves are created.
Note on A94: Jerold Jay: This is the number of (same type) filters that "see" the air flow. The CFM is devided by this number for the satic drop equations. Ex. If you have 4 filters side by side then this number should be 4. This applies to side by side filters only. If it requires two 2" Aluminum Mesh filters to fill the cabinet width and depth then the number should be 2
Note on A121: Jerold Jay: This is the number of (same type) filters that "see" the air flow. The CFM is devided by this number for the satic drop equations. Ex. If you have 4 filters side by side then this number should be 4. This applies to side by side filters only. If it requires two 2" Aluminum Mesh filters to fill the cabinet width and depth then the number should be 2
Note on A150: Jerold Jay: This is the number of (same type) filters that "see" the air flow. The CFM is devided by this number for the satic drop equations. Ex. If you have 4 filters side by side then this number should be 4. This applies to side by side filters only. If it requires two bag filters to fill the cabinet width and depth then the number should be 2
Note on A176: Jerold Jay: This is the number of (same type) filters that "see" the air flow. The CFM is devided by this number for the satic drop equations. Ex. If you have 4 filters side by side then this number should be 4. This applies to side by side filters only. If it requires two HEPA filters to fill the cabinet width and depth then the number should be 2.
Note on C5: Jerold: This line is to connect the end of the High curve to the end of the Low curve. This data is only used on the curve to the left. This function is also performed by the last filter operation.
Note on F193: Jerold Jay: This line connects the endpoint of the "High RPM" curve to the end of the "Low RPM" curve.
Note on G28: Jerold Jay: For each option there is a high and a low RPM Curve. For any option, (example 2HP Low Static) both curves will be used. The curve for the Higher RPM (1375 RPM) is used under the High RPM section and the curve for Lower RPM (1150 RPM) is used in the low RPM section.
Note on G29: Jerold: This is the high rpm/static curve on the chart. All collumns should have zeros except: the column for the motor selected (C2) and the Sum column. The sum column is the one used for the calculations (for curves generated by the options below.)
Note on M29: Jerold: This is the low rpm/static curve on the chart. All collumns should have zeros except: the column for the motor selected (C2) and the Sum column. The sum column is the one used for the calculations (for curves generated by the options below.)