## Interface
Motor Blower
First Pre-Fitler
Second Pre-Fitler
Bag Filter
Afterfilter
Number of 16" Inlets
Number of 14" Inlets
Number of 12" Inlets
Number of 10" Inlets
Number of Inlets Used | 3
Do NOT use data beyond the endpoint of the curve. The endpoint indicates overcurrent conditions of the motor.

## Options (hidden)
Motor Blower
Choose a blower
1530 RPM
1675 RPM
1800 RPM
1950 RPM
First Pre-Fitler
No Prefilter
2" Aluminum Mesh
2" Baffle Impinger
2" Pleated Prefilter
4" Pleated Prefilter
Pink & White MaxiGrid Panel
Second Pre-Fitler
No Prefilter
2" Aluminum Mesh
2" Baffle Impinger
2" Pleated Prefilter
Pink & White MaxiGrid Panel
Bag Filter
No Bag Filter
55% Bag Filter
95% Bag Filter
95% Oil Mist Bag Filter
Afterfilter
No After Filter
99.97% Afterfilter
95.99% Afterfilter
Inlets
0
1
2
3

## Blower Curves (hidden)
Fan A
1530 RPM
Static
CFM | Pressure
0 | 5.9
500 | 5.4
1000 | 5.05
1500 | 4.75
2000 | 4.55
2500 | 4.5
3000 | 4.75
3500 | 5
4000 | 5.25
4500 | 5.35
5000 | 5.4
5500 | 5.5
6000 | 5.4
6500 | 5.35
7000 | 5.2
7500 | 5
8000 | 4.9
8500 | 4.75
9000 | 4.5
Fan D
1675 RPM
Static
CFM | Pressure
0 | 7
500 | 6.5
1000 | 6.1
1500 | 5.75
2000 | 5.65
2500 | 5.6
3000 | 5.65
3500 | 5.8
4000 | 6.1
4500 | 6.35
5000 | 6.45
5500 | 6.55
6000 | 6.6
6500 | 6.5
7000 | 6.4
7500 | 6.25
8000 | 6.1
8500
9000

## Filter Curves (hidden)
2" MESH | P3459
S.P. | CFM
0 | 350
0.01 | 500
0.025 | 750
0.04 | 1000
0.06 | 1200
0.09 | 1500
2" BAFFLE | P3460
S.P. | CFM
0.13 | 350
0.24 | 500
0.58 | 750
1.04 | 1000
1.56 | 1200
2.24 | 1500
PINK FILTER
S.P. | CFM
0.07 | 350
0.12 | 500
0.24 | 750
0.38 | 1000
0.52 | 1200
0.7 | 1500
2" PLEAT
S.P. | CFM
0.06 | 350
0.1 | 500
0.2 | 750
0.32 | 1000
0.44 | 1250
0.6 | 1500
4"PLEAT
S.P. | CFM
0.02 | 350
0.04 | 500
0.1 | 750
0.18 | 1000
0.26 | 1250
0.37 | 1500
55% BAG | P3464
S.P. | CFM
0.08 | 350
0.1 | 500
0.18 | 750
0.28 | 1000
0.34 | 1250
0.45 | 1500
95% BAG | P3463
S.P. | CFM
0.09 | 350
0.13 | 500
0.21 | 750
0.31 | 1000
0.37 | 1250
0.48 | 1500
95% OIL MIST | P3465
S.P. | CFM
0.12 | 350
0.15 | 500
0.22 | 750
0.37 | 1000
0.45 | 1200
0.58 | 1500
95% OIL BAG | 2"BAFFLE, 2" MESH
S.P. | CFM
0.27 | 350
0.39 | 500
0.82 | 750
1.37 | 1000
1.95 | 1200
2.45 | 1500
95% Hepa After Fitler
SP | CFM
0.058594 | 0
0.11719 | 200
0.17625 | 400
0.24375 | 600
0.30469 | 800
0.30469 | 1000
0.39375 | 1200
0.51562 | 1400
0.60938 | 1600
0.75 | 1800
0.82031 | 2000
0.98438 | 2200
1.0547 | 2400
1.1719 | 2600
1.2891 | 2800
1.4062 | 3000
99.97% hepa After Fitler
SP | CFM
0.09375 | 160
0.1875 | 325
0.28125 | 475
0.375 | 610
0.51562 | 835
0.65625 | 1010
0.79688 | 1205
0.84375 | 1265
0.98438 | 1465
1.125 | 1660
1.2656 | 1775
1.4062 | 1940
1.5469 | 2125
1.5938 | 2225
1.7344 | 2360
1.875 | 2525
95% OIL BAG | 2"MESH, PINK
S.P. | CFM
0.22 | 350
0.45 | 500
0.61 | 750
0.8 | 1000
1.01 | 1200
1.33 | 1500
95% OIL BAG | 2" MESH
S.P. | CFM
0.13 | 350
0.15 | 500
0.28 | 750
0.42 | 1000
0.52 | 1200
0.65 | 1500

## Equations (hidden)
Component | Equation of Line (Static Pressure and CFM)
1530 RPM | y = -0.000000097465734x2 + 0.000085779905871x + 4.025437966831500
1675 RPM | y = -0.000000126325649x2 + 0.000221503073322x + 4.711300096849680
1800 RPM | y = -0.000000106707200x2 + 0.000150221363082x + 5.898757591345210
1950 RPM | y = -0.000000094033262x2 + 0.000080271122799x + 6.454793623829400
2" Aluminum Mesh | y = 0.000000027778125x2 + 0.000025558846282x - 0.011118973527038
2" Baffle Impinger | y = 0.000000827485548x2 + 0.000351323230831x - 0.121103222269235
2" Pleated Prefilter | y = 0.000000152087912x2 + 0.000188967032967x - 0.027516483516485
4" Pleated Prefilter | y = 0.000000128608059x2 + 0.000068045787546x - 0.022203296703298
Pink & White | y = 0.000000133866081x2 + 0.000312241919292x - 0.062979812520394
55% Bag Filter | y = 0.000000064578755x2 + 0.000206866300366x - 0.007983516483517
95% Bag Filter | y = 0.000000033443223x2 + 0.000275089743590x - 0.012324175824177
95% Oil Mist Bag Filter | y = 0.000000092170102x2 + 0.000247631177727x + 0.009849655808939
99.97% Hepa (Not Available) | y = 0.000000058847975x2 + 0.000602473278352x - 0.014250800111589
95% Hepa (Not Available) | y = 0.000000077917788x2 + 0.000223584640888x + 0.060607192095590

## Data (hidden)
Motor Blower
Choose a blower | 4
1 = 1530 RPM
2 = 1675 RPM | 1 | 6.4549
3 = 1800 RPM | 501 | 6.4714
4 = 1950 RPM | 1001 | 6.4409
| 1501 | 6.3634
| 2001 | 6.2389
| 2501 | 6.0674
| 2501 | 6.0674
| 2501 | 6.0674
| 2501 | 6.0674
| 2501 | 6.0674
| 2501 | 6.0674
| 2501 | 6.0674
| 2501 | 6.0674
| 2501 | 6.0674
| 2501 | 6.0674
| 2501 | 6.0674
| 2501 | 6.0674
| 2501 | 6.0674
First Pre-Fitler
1= No Prefilter
2= 2" Aluminum Mesh | 4
3= 2" Baffle Impinger
4= 2" Pleated Prefilter | 1 | 6.4823
5= 4" Pleated Prefilter | 501 | 6.4729
6= Pink & White MaxiGrid Panel | 1001 | 6.4116
| 1501 | 6.2986
| 2001 | 6.1338
| 2501 | 5.9173
| 2501 | 5.9173
| 2501 | 5.9173
| 2501 | 5.9173
| 2501 | 5.9173
| 2501 | 5.9173
| 2501 | 5.9173
Cell to copy | 2501 | 5.9173
4.0674 | 2501 | 5.9173
| 2501 | 5.9173
| 2501 | 5.9173
| 2501 | 5.9173
| 2501 | 5.9173
Second Pre-Fitler
1= No Prefilter
2= 2" Aluminum Mesh | 2
3= 2" Baffle Impinger
4= 2" Pleated Prefilter | 1 | 6.4935
5= Pink & White MaxiGrid Panel | 501 | 6.4804
| 1001 | 6.4146
| 1501 | 6.2962
| 2001 | 6.1252
| 2501 | 5.9016
| 2501 | 5.9016
| 2501 | 5.9016
| 2501 | 5.9016
| 2501 | 5.9016
| 2501 | 5.9016
| 2501 | 5.9016
| 2501 | 5.9016
| 2501 | 5.9016
| 2501 | 5.9016
| 2501 | 5.9016
| 2501 | 5.9016
| 2501 | 5.9016
Bag Filter
1= No Bag Filter
2 = 55% Bag Filter | 4
3 = 95% Bag Filter
4 = 95% Oil Mist Bag Filter | 1 | 6.4835
| 501 | 6.438
| 1001 | 6.337
| 1501 | 6.1805
| 2001 | 5.9684
| 2501 | 5.7008
| 2501 | 5.7008
| 2501 | 5.7008
| 2501 | 5.7008
| 2501 | 5.7008
| 2501 | 5.7008
| 2501 | 5.7008
| 2501 | 5.7008
| 2501 | 5.7008
| 2501 | 5.7008
| 2501 | 5.7008
| 2501 | 5.7008
| 2501 | 5.7008
Afterfilter
1= No After Filter
2=99.97% Hepa (Not Available) | 1
3= 95% Hepa (Not Available)
| 1 | 6.4835
| 501 | 6.438
| 1001 | 6.337
| 1501 | 6.1805
| 2001 | 5.9684
| 2501 | 5.7008
| 2501 | 5.7008
| 2501 | 5.7008
| 2501 | 5.7008
| 2501 | 5.7008
| 2501 | 5.7008
| 2501 | 5.7008
| 2501 | 5.7008
| 2501 | 5.7008
| 2501 | 5.7008
| 2501 | 5.7008
| 2501 | 5.7008
| 2501 | 5.7008
Entry Loss Factor (per VP) |  |  |  |  | # Of Inlets
0.93 |  |  |  | 3 Opening Check==> | 3
|  | Quantity |  | Quantity |  | Quantity |  | Quantity
Inlet posibilities |  | 4 |  | 1 |  | 1 |  | 1
3-Open-Intets | 16" | 3 | 14" | 0 | 12" | 0 | 10" | 0
3-16" | Area => | 4.1887 | Area => | 0 | Area => | 0 | Area => | 0
2-16" 1-14"
2-16" 1-12" | 1 | 6.4835
2-16" 1-10" | 501 | 6.4372
1-16" 2-14" | 1001 | 6.3337
1-16" 1-14" 1-12" | 1501 | 6.173
1-16" 1-14" 1-10" | 2001 | 5.9552
1-16" 2-12" | 2501 | 5.6802
1-16" 1-12" 1-10" | 2501 | 5.6802
1-16" 2-10" | 2501 | 5.6802
3-14" | 2501 | 5.6802
2-14" 1-12" | 2501 | 5.6802
2-14" 1-10" | 2501 | 5.6802
1-14" 2-12" | 2501 | 5.6802
1-14" 1-12" 1-10" | 2501 | 5.6802
1-14" 2-10" | 2501 | 5.6802
3-12" | 2501 | 5.6802
2-12" 1-10" | 2501 | 5.6802
1-12" 2-10" | 2501 | 5.6802
3-10" | 2501 | 5.6802
2-Open-Intets
2-16"
1-16" 1-14"
1-16" 1-12"
1-16" 1-10"
2-14"
1-14" 1-12"
1-14" 1-10"
2-12"
1-12" 1-10"
2-10"
1-Open-Intet
1-16"
1-14"
1-12"
1-10"

## Fan Confirm Explanation (hidden)
Use of Lau Blower curves proved to be ineffective due to Ideal test conditions used by Lau. We decided to "back into" the fan curves by comparing the data accumulated for filters and the system values tested during MX6000 development. Shaun Ray went throught he test data to determine the validity of testing. Developement of the fan curve from previous test data was done as a joint project between Shau Ray and Jerold Jay.

## Fan Confirm1 (1530 RPM) (hidden)
Filter Testing 1530 RPM
Test Data developed for OM6000DD |  | Test data taken from testing done on MX6000
95% Oil Bag
2" Pleat, 2" Baffle | CFM | System | Sum | SP | CFM
-0.30205 | 0 | 3.9243 | 3.6222 | 0 | 4350
-0.21871 | 250 | 3.8879 | 3.6692 | 0.25 | 4200
-0.13242 | 500 | 3.8282 | 3.6958 | 0.5 | 4030
-0.043187 | 750 | 3.7453 | 3.7022 | 0.75 | 3800
0.048989 | 1000 | 3.6392 | 3.6882 | 1 | 3620
0.14411 | 1250 | 3.5098 | 3.6539 | 1.25 | 3580
0.24217 | 1500 | 3.3571 | 3.5993 | 1.5 | 3420
0.34318 | 1750 | 3.1812 | 3.5244 | 1.75 | 3140
0.44713 | 2000 | 2.9821 | 3.4292 | 2 | 3050
0.55403 | 2250 | 2.7596 | 3.3137 | 2.25 | 2700
0.66386 | 2500 | 2.514 | 3.1778 | 2.5 | 2600
0.77665 | 2750 | 2.245 | 3.0217 | 2.75 | 2220
0.89237 | 3000 | 1.9529 | 2.8452 | 3 | 1720
1.011 | 3250 | 1.6374 | 2.6485 | 3.25 | 1680
1.1327 | 3500 | 1.2987 | 2.4314 | 3.5 | 1500
1.2572 | 3750 | 0.93679 | 2.194
1.3847 | 4000 | 0.5516 | 1.9363 |  |  | 95% Oil Bag | 2" Pleat, 2" Baffle
1.5152 | 4250 | 0.14315 | 1.6583 |  |  | y = 0.000000376793453x2 + 0.001309973237466x - 0.302053555111048
1.6485 | 4500 | -0.28855 | 1.36
1.7849 | 4750 | -0.7435 | 1.0414
1.9242 | 5000 | -1.2217 | 0.70245
2.0664 | 5250 | -1.7232 | 0.3432
2.2115 | 5500 | -2.2479 | -0.036347
2.3596 | 5750 | -2.7958 | -0.43621
2.5107 | 6000 | -3.3671 | -0.85638
2.6647 | 6250 | -3.9615 | -1.2969
2.8216 | 6500 | -4.5793 | -1.7576
2.9815 | 6750 | -5.2203 | -2.2387
3.1443 | 7000 | -5.8845 | -2.7402

## Fan Confirm 2 (1530 RPM) (hidden)
Filter Testing 1530 RPM
Test Data developed for OM6000DD |  |  |  |  | Test data taken from testing done on MX6000
2" Mesh | 2" Pleat | 95% Oil Bag | Sum of Filters | CFM | System | Sum | SP | CFM
-0.011119 | -0.027516 | -0.012324 | -0.05096 | 0 | 4.0764 | 4.0254 | 1 | 5100
-0.009413 | -0.015112 | 0.0049996 | -0.019525 | 250 | 4.0603 | 4.0408 | 1.25 | 4920
-0.0074901 | -0.0015192 | 0.022585 | 0.013575 | 500 | 4.0304 | 4.044 | 1.5 | 4620
-0.0053501 | 0.013262 | 0.040431 | 0.048342 | 750 | 3.9866 | 4.0349 | 1.75 | 4410
-0.0029931 | 0.029231 | 0.058538 | 0.084776 | 1000 | 3.929 | 4.0138 | 2 | 4200
-0.00041913 | 0.046388 | 0.076907 | 0.12288 | 1250 | 3.8575 | 3.9804 | 2.25 | 3900
0.0023719 | 0.064734 | 0.095537 | 0.16264 | 1500 | 3.7722 | 3.9348 | 2.5 | 3600
0.0053799 | 0.084267 | 0.11443 | 0.20408 | 1750 | 3.673 | 3.8771 | 2.75 | 3320
0.008605 | 0.10499 | 0.13358 | 0.24718 | 2000 | 3.56 | 3.8071 | 3 | 2800
0.012047 | 0.1269 | 0.153 | 0.29194 | 2250 | 3.4331 | 3.725 | 3.25 | 2650
0.015706 | 0.15 | 0.17267 | 0.33837 | 2500 | 3.2924 | 3.6307 | 3.5 | 2240
0.019582 | 0.17428 | 0.19261 | 0.38647 | 2750 | 3.1378 | 3.5242 | 3.75 | 1500
0.023675 | 0.19976 | 0.2128 | 0.43624 | 3000 | 2.9693 | 3.4056
0.027985 | 0.22642 | 0.23326 | 0.48767 | 3250 | 2.7871 | 3.2747
0.032513 | 0.25427 | 0.25398 | 0.54077 | 3500 | 2.5909 | 3.1317
0.037257 | 0.28331 | 0.27497 | 0.59553 | 3750 | 2.381 | 2.9765
0.042218 | 0.31354 | 0.29621 | 0.65197 | 4000 | 2.1571 | 2.8091 |  |  |  | System Curve Equation
0.047396 | 0.34495 | 0.31771 | 0.71006 | 4250 | 1.9195 | 2.6295 |  |  | y = -0.000000110797563x2 - 0.000036623999839x + 4.076397599699190
0.052791 | 0.37756 | 0.33948 | 0.76983 | 4500 | 1.6679 | 2.4378
0.058404 | 0.41135 | 0.36151 | 0.83126 | 4750 | 1.4026 | 2.2338
0.064233 | 0.44633 | 0.38379 | 0.89436 | 5000 | 1.1233 | 2.0177
0.070279 | 0.4825 | 0.40634 | 0.95912 | 5250 | 0.83026 | 1.7894
0.076542 | 0.51985 | 0.42915 | 1.0255 | 5500 | 0.52334 | 1.5489
0.083023 | 0.5584 | 0.45222 | 1.0936 | 5750 | 0.20257 | 1.2962
0.08972 | 0.59813 | 0.47556 | 1.1634 | 6000 | -0.13206 | 1.0314
0.096634 | 0.63905 | 0.49915 | 1.2348 | 6250 | -0.48053 | 0.75431
0.10377 | 0.68116 | 0.52301 | 1.3079 | 6500 | -0.84286 | 0.46508
0.11111 | 0.72446 | 0.54712 | 1.3827 | 6750 | -1.219 | 0.16367
0.11868 | 0.76895 | 0.5715 | 1.4591 | 7000 | -1.6091 | -0.14992
95% Oil Bag
y = 0.000000033443223x2 + 0.000275089743590x - 0.012324175824177
2" Mesh
y = 0.000000027778125x2 + 0.000025558846282x - 0.011118973527038
2" Pleat
y = 0.000000152087912x2 + 0.000188967032967x - 0.027516483516485

## Fan Confirm 3 (1530 RPM) (hidden)
Filter Testing 1530 RPM
Test Data developed for OM6000DD |  |  |  |  | Test data taken from testing done on MX6000
Empty | 4" Pleat | 55% Bag | Sum of Filters | CFM | System | Sum | SP | CFM
0 | -0.022203 | -0.0079835 | -0.030187 | 0 | 3.668 | 3.6378 | 1.5 | 5300
0 | -0.017448 | 0.0051979 | -0.01225 | 250 | 3.7297 | 3.7175 | 1.75 | 5100
0 | -0.011688 | 0.018884 | 0.0071957 | 500 | 3.7752 | 3.7824 | 2 | 4800
0 | -0.0049233 | 0.033074 | 0.028151 | 750 | 3.8044 | 3.8325 | 2.25 | 4550
0 | 0.0028462 | 0.047769 | 0.050615 | 1000 | 3.8173 | 3.8679 | 2.5 | 4250
0 | 0.01162 | 0.062969 | 0.074589 | 1250 | 3.814 | 3.8886 | 2.75 | 3800
0 | 0.021399 | 0.078673 | 0.10007 | 1500 | 3.7945 | 3.8945 | 3 | 3520
0 | 0.032183 | 0.094881 | 0.12706 | 1750 | 3.7587 | 3.8857 | 3.25 | 3140
0 | 0.043972 | 0.11159 | 0.15557 | 2000 | 3.7066 | 3.8622 | 3.5 | 3000
0 | 0.056765 | 0.12881 | 0.18558 | 2250 | 3.6383 | 3.8239 | 3.75 | 1600
0 | 0.070563 | 0.14653 | 0.2171 | 2500 | 3.5538 | 3.7709
0 | 0.085366 | 0.16476 | 0.25013 | 2750 | 3.453 | 3.7031
0 | 0.10117 | 0.18349 | 0.28466 | 3000 | 3.3359 | 3.6206
0 | 0.11799 | 0.20273 | 0.32071 | 3250 | 3.2026 | 3.5234
0 | 0.1358 | 0.22247 | 0.35827 | 3500 | 3.0531 | 3.4114
0 | 0.15462 | 0.24271 | 0.39734 | 3750 | 2.8873 | 3.2846
0 | 0.17445 | 0.26346 | 0.43791 | 4000 | 2.7053 | 3.1432 |  |  |  | System Curve Equation
0 | 0.19528 | 0.28472 | 0.48 | 4250 | 2.507 | 2.987 |  |  | y = -0.000000129995740x2 + 0.000279292243639x + 3.668029564394030
0 | 0.21712 | 0.30647 | 0.52359 | 4500 | 2.2924 | 2.816
0 | 0.23996 | 0.32874 | 0.56869 | 4750 | 2.0616 | 2.6303
0 | 0.2638 | 0.3515 | 0.61531 | 5000 | 1.8146 | 2.4299
0 | 0.28865 | 0.37478 | 0.66343 | 5250 | 1.5513 | 2.2147
0 | 0.31451 | 0.39855 | 0.71306 | 5500 | 1.2718 | 1.9848
0 | 0.34137 | 0.42283 | 0.7642 | 5750 | 0.97598 | 1.7402
0 | 0.36923 | 0.44762 | 0.81685 | 6000 | 0.66394 | 1.4808
0 | 0.3981 | 0.47291 | 0.87101 | 6250 | 0.33565 | 1.2067
0 | 0.42798 | 0.4987 | 0.92668 | 6500 | -0.0088909 | 0.91779
0 | 0.45886 | 0.525 | 0.98386 | 6750 | -0.36968 | 0.61418
0 | 0.49074 | 0.5518 | 1.0425 | 7000 | -0.74672 | 0.29583
55% Bag
y = 0.000000064578755x2 + 0.000206866300366x - 0.007983516483517
4" Pleat
y = 0.000000128608059x2 + 0.000068045787546x - 0.022203296703298

## Comparison 1 (hidden)
Filter Testing 1530 RPM
| Sum of Filters | Sum of Filters | Fan Curve From | Curve | Curve
CFM | 95% Oil, Mesh, Pleat | 55% Bag, 4" Pleat | 95% Oil, Mesh, Pleat | 95% Oil, Mesh, Pleat | 55% Bag, 4" Pleat
0 | -0.30205 | -0.05096 | 4.0254 | 4.3275 | 4.0764
250 | -0.21871 | -0.019525 | 4.0408 | 4.2595 | 4.0603
500 | -0.13242 | 0.013575 | 4.044 | 4.1764 | 4.0304
750 | -0.043187 | 0.048342 | 4.0349 | 4.0781 | 3.9866
1000 | 0.048989 | 0.084776 | 4.0138 | 3.9648 | 3.929
1250 | 0.14411 | 0.12288 | 3.9804 | 3.8363 | 3.8575
1500 | 0.24217 | 0.16264 | 3.9348 | 3.6926 | 3.7722
1750 | 0.34318 | 0.20408 | 3.8771 | 3.5339 | 3.673
2000 | 0.44713 | 0.24718 | 3.8071 | 3.36 | 3.56
2250 | 0.55403 | 0.29194 | 3.725 | 3.171 | 3.4331
2500 | 0.66386 | 0.33837 | 3.6307 | 2.9669 | 3.2924
2750 | 0.77665 | 0.38647 | 3.5242 | 2.7476 | 3.1378
3000 | 0.89237 | 0.43624 | 3.4056 | 2.5132 | 2.9693
3250 | 1.011 | 0.48767 | 3.2747 | 2.2637 | 2.7871
3500 | 1.1327 | 0.54077 | 3.1317 | 1.9991 | 2.5909
3750 | 1.2572 | 0.59553 | 2.9765 | 1.7193 | 2.381
4000 | 1.3847 | 0.65197 | 2.8091 | 1.4244 | 2.1571
4250 | 1.5152 | 0.71006 | 2.6295 | 1.1144 | 1.9195
4500 | 1.6485 | 0.76983 | 2.4378 | 0.78922 | 1.6679
4750 | 1.7849 | 0.83126 | 2.2338 | 0.44894 | 1.4026
5000 | 1.9242 | 0.89436 | 2.0177 | 0.093541 | 1.1233
5250 | 2.0664 | 0.95912 | 1.7894 | -0.27699 | 0.83026
5500 | 2.2115 | 1.0255 | 1.5489 | -0.66265 | 0.52334
5750 | 2.3596 | 1.0936 | 1.2962 | -1.0634 | 0.20257
6000 | 2.5107 | 1.1634 | 1.0314 | -1.4793 | -0.13206
6250 | 2.6647 | 1.2348 | 0.75431 | -1.9104 | -0.48053
6500 | 2.8216 | 1.3079 | 0.46508 | -2.3565 | -0.84286
6750 | 2.9815 | 1.3827 | 0.16367 | -2.8178 | -1.219
7000 | 3.1443 | 1.4591 | -0.14992 | -3.2943 | -1.6091

## Fan Confirm 1 (1675 RPM) (hidden)
Filter Testing 1675 RPM
Test Data developed for OM6000DD |  |  |  |  | Test data taken from testing done on MX6000
2" Mesh | 2" Pleat | 95% Oil Bag | Sum of Filters | CFM | System | Sum | SP | CFM
-0.011119 | -0.027516 | -0.012324 | -0.05096 | 0 | 4.7623 | 4.7113 | 1.75 | 5000
-0.009413 | -0.015112 | 0.0049996 | -0.019525 | 250 | 4.7783 | 4.7588 | 2 | 4800
-0.0074901 | -0.0015192 | 0.022585 | 0.013575 | 500 | 4.7769 | 4.7905 | 2.25 | 4610
-0.0053501 | 0.013262 | 0.040431 | 0.048342 | 750 | 4.758 | 4.8064 | 2.5 | 4350
-0.0029931 | 0.029231 | 0.058538 | 0.084776 | 1000 | 4.7217 | 4.8065 | 2.75 | 4200
-0.00041913 | 0.046388 | 0.076907 | 0.12288 | 1250 | 4.6679 | 4.7908 | 3 | 3950
0.0023719 | 0.064734 | 0.095537 | 0.16264 | 1500 | 4.5967 | 4.7593 | 3.25 | 3750
0.0053799 | 0.084267 | 0.11443 | 0.20408 | 1750 | 4.508 | 4.7121 | 3.5 | 3410
0.008605 | 0.10499 | 0.13358 | 0.24718 | 2000 | 4.4018 | 4.649 | 3.75 | 3100
0.012047 | 0.1269 | 0.153 | 0.29194 | 2250 | 4.2782 | 4.5702 | 4 | 2600
0.015706 | 0.15 | 0.17267 | 0.33837 | 2500 | 4.1371 | 4.4755 | 4.25 | 2200
0.019582 | 0.17428 | 0.19261 | 0.38647 | 2750 | 3.9786 | 4.3651 | 4.5 | 1600
0.023675 | 0.19976 | 0.2128 | 0.43624 | 3000 | 3.8026 | 4.2389 | 4.75 | 1300
0.027985 | 0.22642 | 0.23326 | 0.48767 | 3250 | 3.6092 | 4.0969
0.032513 | 0.25427 | 0.25398 | 0.54077 | 3500 | 3.3983 | 3.9391
0.037257 | 0.28331 | 0.27497 | 0.59553 | 3750 | 3.1699 | 3.7655
0.042218 | 0.31354 | 0.29621 | 0.65197 | 4000 | 2.9241 | 3.5761 |  |  |  | System Curve Equation
0.047396 | 0.34495 | 0.31771 | 0.71006 | 4250 | 2.6609 | 3.3709 |  |  | y = -0.000000139657478x2 + 0.000099099167612x + 4.762259729717390
0.052791 | 0.37756 | 0.33948 | 0.76983 | 4500 | 2.3801 | 3.15
0.058404 | 0.41135 | 0.36151 | 0.83126 | 4750 | 2.082 | 2.9132
0.064233 | 0.44633 | 0.38379 | 0.89436 | 5000 | 1.7663 | 2.6607
0.070279 | 0.4825 | 0.40634 | 0.95912 | 5250 | 1.4332 | 2.3923
0.076542 | 0.51985 | 0.42915 | 1.0255 | 5500 | 1.0827 | 2.1082
0.083023 | 0.5584 | 0.45222 | 1.0936 | 5750 | 0.71465 | 1.8083
0.08972 | 0.59813 | 0.47556 | 1.1634 | 6000 | 0.32919 | 1.4926
0.096634 | 0.63905 | 0.49915 | 1.2348 | 6250 | -0.073741 | 1.1611
0.10377 | 0.68116 | 0.52301 | 1.3079 | 6500 | -0.49412 | 0.81381
0.11111 | 0.72446 | 0.54712 | 1.3827 | 6750 | -0.93196 | 0.45073
0.11868 | 0.76895 | 0.5715 | 1.4591 | 7000 | -1.3873 | 0.071865
95% Oil Bag
y = 0.000000033443223x2 + 0.000275089743590x - 0.012324175824177
2" Mesh
y = 0.000000027778125x2 + 0.000025558846282x - 0.011118973527038
2" Pleat
y = 0.000000152087912x2 + 0.000188967032967x - 0.027516483516485

## Fan Confirm 2 (1675 RPM) (hidden)
Filter Testing 1675 RPM
Test Data developed for OM6000DD |  |  |  |  | Test data taken from testing done on MX6000
Empty | 4" Pleat | 55% Bag | Sum of Filters | CFM | System | Sum | SP | CFM
0 | -0.022203 | -0.0079835 | -0.030187 | 0 | 5.2356 | 5.2054 | 1.75 | 5500
0 | -0.017448 | 0.0051979 | -0.01225 | 250 | 5.1832 | 5.1709 | 2 | 5400
0 | -0.011688 | 0.018884 | 0.0071957 | 500 | 5.1215 | 5.1287 | 2.25 | 5225
0 | -0.0049233 | 0.033074 | 0.028151 | 750 | 5.0507 | 5.0789 | 2.5 | 5125
0 | 0.0028462 | 0.047769 | 0.050615 | 1000 | 4.9707 | 5.0213 | 2.75 | 4725
0 | 0.01162 | 0.062969 | 0.074589 | 1250 | 4.8815 | 4.9561 | 3 | 4325
0 | 0.021399 | 0.078673 | 0.10007 | 1500 | 4.7832 | 4.8832 | 3.25 | 4200
0 | 0.032183 | 0.094881 | 0.12706 | 1750 | 4.6756 | 4.8027 | 3.5 | 3800
0 | 0.043972 | 0.11159 | 0.15557 | 2000 | 4.5589 | 4.7144 | 3.75 | 3450
0 | 0.056765 | 0.12881 | 0.18558 | 2250 | 4.4329 | 4.6185 | 4 | 3000
0 | 0.070563 | 0.14653 | 0.2171 | 2500 | 4.2978 | 4.5149 | 4.25 | 2400
0 | 0.085366 | 0.16476 | 0.25013 | 2750 | 4.1535 | 4.4037 | 4.5 | 1600
0 | 0.10117 | 0.18349 | 0.28466 | 3000 | 4.0001 | 4.2847 | 4.75 | 1250
0 | 0.11799 | 0.20273 | 0.32071 | 3250 | 3.8374 | 4.1581 | 5 | 1200
0 | 0.1358 | 0.22247 | 0.35827 | 3500 | 3.6655 | 4.0238 | 5.25 | 775
0 | 0.15462 | 0.24271 | 0.39734 | 3750 | 3.4845 | 3.8819
0 | 0.17445 | 0.26346 | 0.43791 | 4000 | 3.2943 | 3.7322 |  |  |  | System Curve Equation
0 | 0.19528 | 0.28472 | 0.48 | 4250 | 3.0949 | 3.5749 |  |  | y = -0.000000073477450x2 - 0.000191415469391x + 5.235599821125230
0 | 0.21712 | 0.30647 | 0.52359 | 4500 | 2.8863 | 3.4099
0 | 0.23996 | 0.32874 | 0.56869 | 4750 | 2.6685 | 3.2372
0 | 0.2638 | 0.3515 | 0.61531 | 5000 | 2.4416 | 3.0569
0 | 0.28865 | 0.37478 | 0.66343 | 5250 | 2.2054 | 2.8689
0 | 0.31451 | 0.39855 | 0.71306 | 5500 | 1.9601 | 2.6732
0 | 0.34137 | 0.42283 | 0.7642 | 5750 | 1.7056 | 2.4698
0 | 0.36923 | 0.44762 | 0.81685 | 6000 | 1.4419 | 2.2588
0 | 0.3981 | 0.47291 | 0.87101 | 6250 | 1.169 | 2.0401
0 | 0.42798 | 0.4987 | 0.92668 | 6500 | 0.88698 | 1.8137
0 | 0.45886 | 0.525 | 0.98386 | 6750 | 0.59573 | 1.5796
0 | 0.49074 | 0.5518 | 1.0425 | 7000 | 0.2953 | 1.3378
55% Bag
y = 0.000000064578755x2 + 0.000206866300366x - 0.007983516483517
4" Pleat
y = 0.000000128608059x2 + 0.000068045787546x - 0.022203296703298

## Comparison 2 (hidden)
Filter Testing 1675 RPM
| Sum of Filters | Sum of Filters | Fan Curve From | Curve | Curve
CFM | 95% Oil, Mesh, Pleat | 55% Bag, 4" Pleat | 95% Oil, Mesh, Pleat | 95% Oil, Mesh, Pleat | 55% Bag, 4" Pleat
0 | -0.05096 | -0.030187 | 4.7113 | 4.7623 | 4.7415
250 | -0.019525 | -0.01225 | 4.7588 | 4.7783 | 4.771
500 | 0.013575 | 0.0071957 | 4.7905 | 4.7769 | 4.7833
750 | 0.048342 | 0.028151 | 4.8064 | 4.758 | 4.7782
1000 | 0.084776 | 0.050615 | 4.8065 | 4.7217 | 4.7559
1250 | 0.12288 | 0.074589 | 4.7908 | 4.6679 | 4.7162
1500 | 0.16264 | 0.10007 | 4.7593 | 4.5967 | 4.6592
1750 | 0.20408 | 0.12706 | 4.7121 | 4.508 | 4.585
2000 | 0.24718 | 0.15557 | 4.649 | 4.4018 | 4.4934
2250 | 0.29194 | 0.18558 | 4.5702 | 4.2782 | 4.3846
2500 | 0.33837 | 0.2171 | 4.4755 | 4.1371 | 4.2584
2750 | 0.38647 | 0.25013 | 4.3651 | 3.9786 | 4.115
3000 | 0.43624 | 0.28466 | 4.2389 | 3.8026 | 3.9542
3250 | 0.48767 | 0.32071 | 4.0969 | 3.6092 | 3.7762
3500 | 0.54077 | 0.35827 | 3.9391 | 3.3983 | 3.5808
3750 | 0.59553 | 0.39734 | 3.7655 | 3.1699 | 3.3681
4000 | 0.65197 | 0.43791 | 3.5761 | 2.9241 | 3.1382
4250 | 0.71006 | 0.48 | 3.3709 | 2.6609 | 2.8909
4500 | 0.76983 | 0.52359 | 3.15 | 2.3801 | 2.6264
4750 | 0.83126 | 0.56869 | 2.9132 | 2.082 | 2.3445
5000 | 0.89436 | 0.61531 | 2.6607 | 1.7663 | 2.0454
5250 | 0.95912 | 0.66343 | 2.3923 | 1.4332 | 1.7289
5500 | 1.0255 | 0.71306 | 2.1082 | 1.0827 | 1.3952
5750 | 1.0936 | 0.7642 | 1.8083 | 0.71465 | 1.0441
6000 | 1.1634 | 0.81685 | 1.4926 | 0.32919 | 0.67574
6250 | 1.2348 | 0.87101 | 1.1611 | -0.073741 | 0.29009
6500 | 1.3079 | 0.92668 | 0.81381 | -0.49412 | -0.11287
6750 | 1.3827 | 0.98386 | 0.45073 | -0.93196 | -0.53312
7000 | 1.4591 | 1.0425 | 0.071865 | -1.3873 | -0.97068

## Fan Confirm 1 (1800 RPM) (hidden)
Filter Testing 1800 RPM
Test Data developed for OM6000DD |  |  |  |  | Test data taken from testing done on MX6000
2" Mesh | 2" Pleat | 95% Oil Bag | Sum of Filters | CFM | System | Sum | SP | CFM
-0.011119 | -0.027516 | -0.012324 | -0.05096 | 0 | 5.9497 | 5.8988 | 4.5 | 3700
-0.009413 | -0.015112 | 0.0049996 | -0.019525 | 250 | 5.9492 | 5.9296 | 4.75 | 3250
-0.0074901 | -0.0015192 | 0.022585 | 0.013575 | 500 | 5.9336 | 5.9472 | 5 | 2800
-0.0053501 | 0.013262 | 0.040431 | 0.048342 | 750 | 5.9031 | 5.9514 | 5.25 | 2100
-0.0029931 | 0.029231 | 0.058538 | 0.084776 | 1000 | 5.8575 | 5.9423 | 5.75 | 1670
-0.00041913 | 0.046388 | 0.076907 | 0.12288 | 1250 | 5.7969 | 5.9198 | 6 | 1360
0.0023719 | 0.064734 | 0.095537 | 0.16264 | 1500 | 5.7214 | 5.884 | 5.875 | 100
0.0053799 | 0.084267 | 0.11443 | 0.20408 | 1750 | 5.6308 | 5.8349
0.008605 | 0.10499 | 0.13358 | 0.24718 | 2000 | 5.5252 | 5.7724
0.012047 | 0.1269 | 0.153 | 0.29194 | 2250 | 5.4046 | 5.6966
0.015706 | 0.15 | 0.17267 | 0.33837 | 2500 | 5.269 | 5.6074
0.019582 | 0.17428 | 0.19261 | 0.38647 | 2750 | 5.1184 | 5.5049
0.023675 | 0.19976 | 0.2128 | 0.43624 | 3000 | 4.9528 | 5.3891
0.027985 | 0.22642 | 0.23326 | 0.48767 | 3250 | 4.7722 | 5.2599
0.032513 | 0.25427 | 0.25398 | 0.54077 | 3500 | 4.5766 | 5.1174
0.037257 | 0.28331 | 0.27497 | 0.59553 | 3750 | 4.366 | 4.9615
0.042218 | 0.31354 | 0.29621 | 0.65197 | 4000 | 4.1404 | 4.7923 |  |  |  | System Curve Equation
0.047396 | 0.34495 | 0.31771 | 0.71006 | 4250 | 3.8997 | 4.6098 |  |  | y = -0.000000120039029x2 + 0.000027817457372x + 5.949717224212920
0.052791 | 0.37756 | 0.33948 | 0.76983 | 4500 | 3.6441 | 4.4139
0.058404 | 0.41135 | 0.36151 | 0.83126 | 4750 | 3.3735 | 4.2047
0.064233 | 0.44633 | 0.38379 | 0.89436 | 5000 | 3.0878 | 3.9822
0.070279 | 0.4825 | 0.40634 | 0.95912 | 5250 | 2.7872 | 3.7463
0.076542 | 0.51985 | 0.42915 | 1.0255 | 5500 | 2.4715 | 3.4971
0.083023 | 0.5584 | 0.45222 | 1.0936 | 5750 | 2.1409 | 3.2345
0.08972 | 0.59813 | 0.47556 | 1.1634 | 6000 | 1.7952 | 2.9586
0.096634 | 0.63905 | 0.49915 | 1.2348 | 6250 | 1.4346 | 2.6694
0.10377 | 0.68116 | 0.52301 | 1.3079 | 6500 | 1.0589 | 2.3668
0.11111 | 0.72446 | 0.54712 | 1.3827 | 6750 | 0.66821 | 2.0509
0.11868 | 0.76895 | 0.5715 | 1.4591 | 7000 | 0.26253 | 1.7217
95% Oil Bag
y = 0.000000033443223x2 + 0.000275089743590x - 0.012324175824177
2" Mesh
y = 0.000000027778125x2 + 0.000025558846282x - 0.011118973527038
2" Pleat
y = 0.000000152087912x2 + 0.000188967032967x - 0.027516483516485

## Fan Confirm 2 (1800 RPM) (hidden)
Filter Testing 1800 RPM
Test Data developed for OM6000DD |  |  |  |  | Test data taken from testing done on MX6000
Empty | 4" Pleat | 55% Bag | Sum of Filters | CFM | System | Sum | SP | CFM
0 | -0.022203 | -0.0079835 | -0.030187 | 0 | 5.9479 | 5.9177 | 4.75 | 3840
0 | -0.017448 | 0.0051979 | -0.01225 | 250 | 5.936 | 5.9238 | 5 | 3190
0 | -0.011688 | 0.018884 | 0.0071957 | 500 | 5.9142 | 5.9214 | 5.25 | 2510
0 | -0.0049233 | 0.033074 | 0.028151 | 750 | 5.8824 | 5.9106 | 5.5 | 1800
0 | 0.0028462 | 0.047769 | 0.050615 | 1000 | 5.8408 | 5.8914 | 5.75 | 1690
0 | 0.01162 | 0.062969 | 0.074589 | 1250 | 5.7893 | 5.8639 | 6 | 1370
0 | 0.021399 | 0.078673 | 0.10007 | 1500 | 5.7278 | 5.8279 | 5.875 | 100
0 | 0.032183 | 0.094881 | 0.12706 | 1750 | 5.6565 | 5.7835
0 | 0.043972 | 0.11159 | 0.15557 | 2000 | 5.5752 | 5.7308
0 | 0.056765 | 0.12881 | 0.18558 | 2250 | 5.4841 | 5.6697
0 | 0.070563 | 0.14653 | 0.2171 | 2500 | 5.383 | 5.6001
0 | 0.085366 | 0.16476 | 0.25013 | 2750 | 5.2721 | 5.5222
0 | 0.10117 | 0.18349 | 0.28466 | 3000 | 5.1512 | 5.4359
0 | 0.11799 | 0.20273 | 0.32071 | 3250 | 5.0205 | 5.3412
0 | 0.1358 | 0.22247 | 0.35827 | 3500 | 4.8798 | 5.2381
0 | 0.15462 | 0.24271 | 0.39734 | 3750 | 4.7292 | 5.1266
0 | 0.17445 | 0.26346 | 0.43791 | 4000 | 4.5688 | 5.0067 |  |  |  | System Curve Equation
0 | 0.19528 | 0.28472 | 0.48 | 4250 | 4.3984 | 4.8784 |  |  | y = -0.000000079222105x2 - 0.000027907579000x + 5.947935241935190
0 | 0.21712 | 0.30647 | 0.52359 | 4500 | 4.2181 | 4.7417
0 | 0.23996 | 0.32874 | 0.56869 | 4750 | 4.0279 | 4.5966
0 | 0.2638 | 0.3515 | 0.61531 | 5000 | 3.8278 | 4.4432
0 | 0.28865 | 0.37478 | 0.66343 | 5250 | 3.6179 | 4.2813
0 | 0.31451 | 0.39855 | 0.71306 | 5500 | 3.398 | 4.111
0 | 0.34137 | 0.42283 | 0.7642 | 5750 | 3.1682 | 3.9324
0 | 0.36923 | 0.44762 | 0.81685 | 6000 | 2.9285 | 3.7453
0 | 0.3981 | 0.47291 | 0.87101 | 6250 | 2.6789 | 3.5499
0 | 0.42798 | 0.4987 | 0.92668 | 6500 | 2.4194 | 3.3461
0 | 0.45886 | 0.525 | 0.98386 | 6750 | 2.15 | 3.1339
0 | 0.49074 | 0.5518 | 1.0425 | 7000 | 1.8707 | 2.9132
55% Bag
y = 0.000000064578755x2 + 0.000206866300366x - 0.007983516483517
4" Pleat
y = 0.000000128608059x2 + 0.000068045787546x - 0.022203296703298

## Comparison 3 (hidden)
Filter Testing 1675 RPM
| Sum of Filters | Sum of Filters | Fan Curve From | Curve | Curve
CFM | 95% Oil, Mesh, Pleat | 55% Bag, 4" Pleat | 95% Oil, Mesh, Pleat | 95% Oil, Mesh, Pleat | 55% Bag, 4" Pleat
0 | -0.05096 | -0.030187 | 5.8988 | 5.9497 | 5.9289
250 | -0.019525 | -0.01225 | 5.9492 | 5.9687 | 5.9614
500 | 0.013575 | 0.0071957 | 5.9336 | 5.92 | 5.9264
750 | 0.048342 | 0.028151 | 5.9031 | 5.8547 | 5.8749
1000 | 0.084776 | 0.050615 | 5.8575 | 5.7727 | 5.8069
1250 | 0.12288 | 0.074589 | 5.7969 | 5.6741 | 5.7223
1500 | 0.16264 | 0.10007 | 5.7214 | 5.5587 | 5.6213
1750 | 0.20408 | 0.12706 | 5.6308 | 5.4267 | 5.5037
2000 | 0.24718 | 0.15557 | 5.5252 | 5.278 | 5.3696
2250 | 0.29194 | 0.18558 | 5.4046 | 5.1127 | 5.219
2500 | 0.33837 | 0.2171 | 5.269 | 4.9306 | 5.0519
2750 | 0.38647 | 0.25013 | 5.1184 | 4.7319 | 4.8683
3000 | 0.43624 | 0.28466 | 4.9528 | 4.5166 | 4.6682
3250 | 0.48767 | 0.32071 | 4.7722 | 4.2845 | 4.4515
3500 | 0.54077 | 0.35827 | 4.5766 | 4.0358 | 4.2183
3750 | 0.59553 | 0.39734 | 4.366 | 3.7704 | 3.9686
4000 | 0.65197 | 0.43791 | 4.1404 | 3.4884 | 3.7025
4250 | 0.71006 | 0.48 | 3.8997 | 3.1897 | 3.4197
4500 | 0.76983 | 0.52359 | 3.6441 | 2.8743 | 3.1205
4750 | 0.83126 | 0.56869 | 3.3735 | 2.5422 | 2.8048
5000 | 0.89436 | 0.61531 | 3.0878 | 2.1935 | 2.4725
5250 | 0.95912 | 0.66343 | 2.7872 | 1.8281 | 2.1238
5500 | 1.0255 | 0.71306 | 2.4715 | 1.446 | 1.7585
5750 | 1.0936 | 0.7642 | 2.1409 | 1.0472 | 1.3767
6000 | 1.1634 | 0.81685 | 1.7952 | 0.63181 | 0.97837
6250 | 1.2348 | 0.87101 | 1.4346 | 0.19971 | 0.56354
6500 | 1.3079 | 0.92668 | 1.0589 | -0.24905 | 0.1322
6750 | 1.3827 | 0.98386 | 0.66821 | -0.71449 | -0.31565
7000 | 1.4591 | 1.0425 | 0.26253 | -1.1966 | -0.78002

## Fan Confirm 1 (1950 RPM) (hidden)
Filter Testing 1950 RPM
Test Data developed for OM6000DD |  |  |  |  | Test data taken from testing done on MX6000
2" Mesh | 2" Pleat | 95% Oil Bag | Sum of Filters | CFM | System | Sum | SP | CFM
-0.011119 | -0.027516 | -0.012324 | -0.05096 | 0 | 6.5058 | 6.4548 | 5.25 | 3225
-0.009413 | -0.015112 | 0.0049996 | -0.019525 | 250 | 6.4885 | 6.469 | 5.5 | 2890
-0.0074901 | -0.0015192 | 0.022585 | 0.013575 | 500 | 6.4578 | 6.4714 | 5.75 | 2430
-0.0053501 | 0.013262 | 0.040431 | 0.048342 | 750 | 6.4138 | 6.4621 | 6 | 2005
-0.0029931 | 0.029231 | 0.058538 | 0.084776 | 1000 | 6.3563 | 6.441 | 6.5 | 100
-0.00041913 | 0.046388 | 0.076907 | 0.12288 | 1250 | 6.2853 | 6.4082
0.0023719 | 0.064734 | 0.095537 | 0.16264 | 1500 | 6.201 | 6.3636
0.0053799 | 0.084267 | 0.11443 | 0.20408 | 1750 | 6.1032 | 6.3073
0.008605 | 0.10499 | 0.13358 | 0.24718 | 2000 | 5.992 | 6.2392
0.012047 | 0.1269 | 0.153 | 0.29194 | 2250 | 5.8674 | 6.1594
0.015706 | 0.15 | 0.17267 | 0.33837 | 2500 | 5.7294 | 6.0678
0.019582 | 0.17428 | 0.19261 | 0.38647 | 2750 | 5.5779 | 5.9644
0.023675 | 0.19976 | 0.2128 | 0.43624 | 3000 | 5.4131 | 5.8493
0.027985 | 0.22642 | 0.23326 | 0.48767 | 3250 | 5.2348 | 5.7224
0.032513 | 0.25427 | 0.25398 | 0.54077 | 3500 | 5.0431 | 5.5838
0.037257 | 0.28331 | 0.27497 | 0.59553 | 3750 | 4.8379 | 5.4335
0.042218 | 0.31354 | 0.29621 | 0.65197 | 4000 | 4.6194 | 5.2713 |  |  |  | System Curve Equation
0.047396 | 0.34495 | 0.31771 | 0.71006 | 4250 | 4.3874 | 5.0975 |  |  | y = -0.000000107365091x2 - 0.000042132782911x + 6.505753256697130
0.052791 | 0.37756 | 0.33948 | 0.76983 | 4500 | 4.142 | 4.9118
0.058404 | 0.41135 | 0.36151 | 0.83126 | 4750 | 3.8832 | 4.7145
0.064233 | 0.44633 | 0.38379 | 0.89436 | 5000 | 3.611 | 4.5053
0.070279 | 0.4825 | 0.40634 | 0.95912 | 5250 | 3.3253 | 4.2844
0.076542 | 0.51985 | 0.42915 | 1.0255 | 5500 | 3.0262 | 4.0518
0.083023 | 0.5584 | 0.45222 | 1.0936 | 5750 | 2.7137 | 3.8074
0.08972 | 0.59813 | 0.47556 | 1.1634 | 6000 | 2.3878 | 3.5512
0.096634 | 0.63905 | 0.49915 | 1.2348 | 6250 | 2.0485 | 3.2833
0.10377 | 0.68116 | 0.52301 | 1.3079 | 6500 | 1.6957 | 3.0037
0.11111 | 0.72446 | 0.54712 | 1.3827 | 6750 | 1.3295 | 2.7122
0.11868 | 0.76895 | 0.5715 | 1.4591 | 7000 | 0.94993 | 2.4091
95% Oil Bag
y = 0.000000033443223x2 + 0.000275089743590x - 0.012324175824177
2" Mesh
y = 0.000000027778125x2 + 0.000025558846282x - 0.011118973527038
2" Pleat
y = 0.000000152087912x2 + 0.000188967032967x - 0.027516483516485

## Fan Confirm 2 (1950 RPM) (hidden)
Filter Testing 1950 RPM
Test Data developed for OM6000DD |  |  |  |  | Test data taken from testing done on MX6000
Empty | 4" Pleat | 55% Bag | Sum of Filters | CFM | System | Sum | SP | CFM
0 | -0.022203 | -0.0079835 | -0.030187 | 0 | 7.1247 | 7.0945 | 5.5 | 3600
0 | -0.017448 | 0.0051979 | -0.01225 | 250 | 6.9991 | 6.9869 | 5.65 | 3210
0 | -0.011688 | 0.018884 | 0.0071957 | 500 | 6.8754 | 6.8826 | 5.75 | 2990
0 | -0.0049233 | 0.033074 | 0.028151 | 750 | 6.7536 | 6.7817 | 5.87 | 2700
0 | 0.0028462 | 0.047769 | 0.050615 | 1000 | 6.6337 | 6.6843 | 6 | 2390
0 | 0.01162 | 0.062969 | 0.074589 | 1250 | 6.5156 | 6.5902
0 | 0.021399 | 0.078673 | 0.10007 | 1500 | 6.3995 | 6.4995
0 | 0.032183 | 0.094881 | 0.12706 | 1750 | 6.2852 | 6.4123
0 | 0.043972 | 0.11159 | 0.15557 | 2000 | 6.1728 | 6.3284
0 | 0.056765 | 0.12881 | 0.18558 | 2250 | 6.0623 | 6.2479
0 | 0.070563 | 0.14653 | 0.2171 | 2500 | 5.9538 | 6.1709
0 | 0.085366 | 0.16476 | 0.25013 | 2750 | 5.8471 | 6.0972
0 | 0.10117 | 0.18349 | 0.28466 | 3000 | 5.7422 | 6.0269
0 | 0.11799 | 0.20273 | 0.32071 | 3250 | 5.6393 | 5.96
0 | 0.1358 | 0.22247 | 0.35827 | 3500 | 5.5383 | 5.8966 | Insufficient Data
0 | 0.15462 | 0.24271 | 0.39734 | 3750 | 5.4391 | 5.8365 | For an Accurate
0 | 0.17445 | 0.26346 | 0.43791 | 4000 | 5.3419 | 5.7798 | Curve |  |  | System Curve Equation
0 | 0.19528 | 0.28472 | 0.48 | 4250 | 5.2465 | 5.7265 |  |  | y = 0.000000015119267x2 - 0.000506182926183x + 7.124715529482000
0 | 0.21712 | 0.30647 | 0.52359 | 4500 | 5.1531 | 5.6766
0 | 0.23996 | 0.32874 | 0.56869 | 4750 | 5.0615 | 5.6302
0 | 0.2638 | 0.3515 | 0.61531 | 5000 | 4.9718 | 5.5871
0 | 0.28865 | 0.37478 | 0.66343 | 5250 | 4.884 | 5.5474
0 | 0.31451 | 0.39855 | 0.71306 | 5500 | 4.7981 | 5.5111
0 | 0.34137 | 0.42283 | 0.7642 | 5750 | 4.714 | 5.4782
0 | 0.36923 | 0.44762 | 0.81685 | 6000 | 4.6319 | 5.4488
0 | 0.3981 | 0.47291 | 0.87101 | 6250 | 4.5517 | 5.4227
0 | 0.42798 | 0.4987 | 0.92668 | 6500 | 4.4733 | 5.4
0 | 0.45886 | 0.525 | 0.98386 | 6750 | 4.3969 | 5.3807
0 | 0.49074 | 0.5518 | 1.0425 | 7000 | 4.3223 | 5.3648
55% Bag
y = 0.000000064578755x2 + 0.000206866300366x - 0.007983516483517
4" Pleat
y = 0.000000128608059x2 + 0.000068045787546x - 0.022203296703298

## Comparison 4 (hidden)
Filter Testing 1950 RPM
| Sum of Filters | Sum of Filters | Fan Curve From | Curve | Curve
CFM | 95% Oil, Mesh, Pleat | 55% Bag, 4" Pleat | 95% Oil, Mesh, Pleat | 95% Oil, Mesh, Pleat | 55% Bag, 4" Pleat
0 | -0.05096 | -0.030187 | 6.4548 | 6.5058 | 6.485
250 | -0.019525 | -0.01225 | 6.4885 | 6.508 | 6.5008
500 | 0.013575 | 0.0071957 | 6.4578 | 6.4443 | 6.4506
750 | 0.048342 | 0.028151 | 6.4138 | 6.3654 | 6.3856
1000 | 0.084776 | 0.050615 | 6.3563 | 6.2715 | 6.3056
1250 | 0.12288 | 0.074589 | 6.2853 | 6.1625 | 6.2107
1500 | 0.16264 | 0.10007 | 6.201 | 6.0383 | 6.1009
1750 | 0.20408 | 0.12706 | 6.1032 | 5.8991 | 5.9762
2000 | 0.24718 | 0.15557 | 5.992 | 5.7449 | 5.8365
2250 | 0.29194 | 0.18558 | 5.8674 | 5.5755 | 5.6818
2500 | 0.33837 | 0.2171 | 5.7294 | 5.391 | 5.5123
2750 | 0.38647 | 0.25013 | 5.5779 | 5.1915 | 5.3278
3000 | 0.43624 | 0.28466 | 5.4131 | 4.9768 | 5.1284
3250 | 0.48767 | 0.32071 | 5.2348 | 4.7471 | 4.9141
3500 | 0.54077 | 0.35827 | 5.0431 | 4.5023 | 4.6848
3750 | 0.59553 | 0.39734 | 4.8379 | 4.2424 | 4.4406
4000 | 0.65197 | 0.43791 | 4.6194 | 3.9674 | 4.1815
4250 | 0.71006 | 0.48 | 4.3874 | 3.6773 | 3.9074
4500 | 0.76983 | 0.52359 | 4.142 | 3.3722 | 3.6184
4750 | 0.83126 | 0.56869 | 3.8832 | 3.0519 | 3.3145
5000 | 0.89436 | 0.61531 | 3.611 | 2.7166 | 2.9957
5250 | 0.95912 | 0.66343 | 3.3253 | 2.3662 | 2.6619
5500 | 1.0255 | 0.71306 | 3.0262 | 2.0007 | 2.3132
5750 | 1.0936 | 0.7642 | 2.7137 | 1.6201 | 1.9495
6000 | 1.1634 | 0.81685 | 2.3878 | 1.2244 | 1.571
6250 | 1.2348 | 0.87101 | 2.0485 | 0.81364 | 1.1775
6500 | 1.3079 | 0.92668 | 1.6957 | 0.38778 | 0.76904
6750 | 1.3827 | 0.98386 | 1.3295 | -0.053163 | 0.34568
7000 | 1.4591 | 1.0425 | 0.94993 | -0.50919 | -0.09261