## Interface
Motor Blower
Choose a blower | 4
1 = 3hp
2 = 5hp
3 = 7.5hp
4 = 10hp
5 = 15hp
First Pre-Fitler
1= No Prefilter | 2
2= 2" Aluminum Mesh
3= 2" Baffle Impinger
4= 2" Pleated Prefilter
5= 4" Pleated Prefilter
6= Pink & White MaxiGrid Panel
Second Pre-Fitler
1= No Prefilter | 5
2= 2" Aluminum Mesh
3= 2" Baffle Impinger
4= 2" Pleated Prefilter
5= Pink & White MaxiGrid Panel
Bag Filter
1= No Bag Filter | 4
2 = 55% Bag Filter
3 = 95% Bag Filter
4 = 95% Oil Mist Bag Filter
Afterfilter | 1
1= No After Filter
2=99.97% Hepa (Not Available)
3= 95% Hepa (Not Available)
Number of 16" Inlets | 3
Number of 14" Inlets | 0
Number of 12" Inlets | 0
Number of 10" Inlets | 0
Number of Inlets Used | 3
Sheet Passwords = metalfab

## Blower Curves (hidden)
Fan A
3 HP HDBI-120
Static
CFM | Pressure
0 | 7
500 | 6.9
1000 | 7
1500 | 6.9
2000 | 6.25
2500 | 4.75
3000 | 2.625
3500 | 0
Fan D
5 HP HDBI-130
Static
CFM | Pressure
0 | 8.5
500 | 8.375
1000 | 8.5
1500 | 8.6
2000 | 8.5
2500 | 7.8
3000 | 6.75
3500 | 5.25
4000 | 3.25
4500 | 1
4700 | 0
Fan G
7.5 HP HDBI-150
Static
CFM | Pressure
0 | 10.5
500 | 10
1000 | 9.9
1500 | 10
2000 | 10.375
2500 | 10.1
3000 | 9.75
3500 | 9
4000 | 7.5
4500 | 6
5000 | 4.25
5500 | 2
6000 | 0
Fan H
10 HP HDBI-160
Static
CFM | Pressure
0 | 12.75
500 | 12
1000 | 11.8
1500 | 12.2
2000 | 12.75
2500 | 12.8
3000 | 12
3500 | 11
4000 | 9.5
4500 | 8
5000 | 6
5500 | 4
6000 | 1.75
6300 | 0
Fan L
15 HP HDBI-160
Static
CFM | Pressure
0 | 12.75
500 | 12.25
1000 | 11.9
1500 | 11.9
2000 | 12.25
2500 | 12.5
3000 | 12.75
3500 | 12.5
4000 | 12
4500 | 11
5000 | 10.25
5500 | 9
6000 | 8
6500 | 6.75
7000 | 5
7500 | 3.25
8000 | 1.5
8300 | 0

## Filter Curves (hidden)
2" MESH | P3459
S.P. | CFM
0 | 350
0.01 | 500
0.025 | 750
0.04 | 1000
0.06 | 1200
0.09 | 1500
2" BAFFLE | P3460
S.P. | CFM
0.13 | 350
0.24 | 500
0.58 | 750
1.04 | 1000
1.56 | 1200
2.24 | 1500
PINK FILTER
S.P. | CFM
0.07 | 350
0.12 | 500
0.24 | 750
0.38 | 1000
0.52 | 1200
0.7 | 1500
2" PLEAT
S.P. | CFM
0.06 | 350
0.1 | 500
0.2 | 750
0.32 | 1000
0.44 | 1250
0.6 | 1500
4"PLEAT
S.P. | CFM
0.02 | 350
0.04 | 500
0.1 | 750
0.18 | 1000
0.26 | 1250
0.37 | 1500
55% BAG | P3464
S.P. | CFM
0.08 | 350
0.1 | 500
0.18 | 750
0.28 | 1000
0.34 | 1250
0.45 | 1500
95% BAG | P3463
S.P. | CFM
0.09 | 350
0.13 | 500
0.21 | 750
0.31 | 1000
0.37 | 1250
0.48 | 1500
95% OIL MIST | P3465
S.P. | CFM
0.12 | 350
0.15 | 500
0.22 | 750
0.37 | 1000
0.45 | 1200
0.58 | 1500
95% OIL BAG | 2"BAFFLE, 2" MESH
S.P. | CFM
0.27 | 350
0.39 | 500
0.82 | 750
1.37 | 1000
1.95 | 1200
2.45 | 1500
95% Hepa After Fitler
SP | CFM
0.058594 | 0
0.11719 | 200
0.17625 | 400
0.24375 | 600
0.30469 | 800
0.30469 | 1000
0.39375 | 1200
0.51562 | 1400
0.60938 | 1600
0.75 | 1800
0.82031 | 2000
0.98438 | 2200
1.0547 | 2400
1.1719 | 2600
1.2891 | 2800
1.4062 | 3000
99.97% hepa After Fitler
SP | CFM
0.09375 | 160
0.1875 | 325
0.28125 | 475
0.375 | 610
0.51562 | 835
0.65625 | 1010
0.79688 | 1205
0.84375 | 1265
0.98438 | 1465
1.125 | 1660
1.2656 | 1775
1.4062 | 1940
1.5469 | 2125
1.5938 | 2225
1.7344 | 2360
1.875 | 2525
95% OIL BAG | 2"MESH, PINK
S.P. | CFM
0.22 | 350
0.45 | 500
0.61 | 750
0.8 | 1000
1.01 | 1200
1.33 | 1500
95% OIL BAG | 2" MESH
S.P. | CFM
0.13 | 350
0.15 | 500
0.28 | 750
0.42 | 1000
0.52 | 1200
0.65 | 1500

## Equations (hidden)
Component | Equation of Line (Static Pressure and CFM)
3HP HDBI-120 | y = 0.000000000000125x4 - 0.000000001078157x3 + 0.000001944412879x2 - 0.000975807178921x + 7.006155303018720
5HP HDBI-130 | y = 0.000000000000046x4 - 0.000000000515665x3 + 0.000001167158259x2 - 0.000672272166264x + 8.491659296094950
7.5HP HDBI-150 | y = 0.000000000000036x4 - 0.000000000491399x3 + 0.000001652055910x2 - 0.001763150207642x + 10.499248545568900
10HP HDBI-160 | y = 0.000000000000038x4 - 0.000000000518486x3 + 0.000001740550130x2 - 0.001775551895914x + 12.605516516310900
15HP HDBI-160 | y = 0.000000000000010x4 - 0.000000000185328x3 + 0.000000826172293x2 - 0.001149994531218x + 12.613581173700300
2" Aluminum Mesh | y = 0.000000027778125x2 + 0.000025558846282x - 0.011118973527038
2" Baffle Impinger | y = 0.000000827485548x2 + 0.000351323230831x - 0.121103222269235
2" Pleated Prefilter | y = 0.000000152087912x2 + 0.000188967032967x - 0.027516483516485
4" Pleated Prefilter | y = 0.000000128608059x2 + 0.000068045787546x - 0.022203296703298
Pink & White | y = 0.000000133866081x2 + 0.000312241919292x - 0.062979812520394
55% Bag Filter | y = 0.000000064578755x2 + 0.000206866300366x - 0.007983516483517
95% Bag Filter | y = 0.000000033443223x2 + 0.000275089743590x - 0.012324175824177
95% Oil Mist Bag Filter | y = 0.000000092170102x2 + 0.000247631177727x + 0.009849655808939
99.97% Hepa (Not Available) | y = 0.000000058847975x2 + 0.000602473278352x - 0.014250800111589
95% Hepa (Not Available) | y = 0.000000077917788x2 + 0.000223584640888x + 0.060607192095590

## Data (hidden)
Motor Blower
Choose a blower | 4
1 = 3hp
2 = 5hp | 0 | 12.6055
3 = 7.5hp | 500 | 12.0904
4 = 10hp | 1000 | 12.09
5 = 15hp | 1500 | 12.3009
| 2000 | 12.4767
| 2500 | 12.4281
| 3000 | 12.0227
| 3500 | 11.1851
| 4000 | 9.897
| 4500 | 8.197
| 5000 | 6.1808
| 5500 | 4.0009
| 6000 | 1.867
| 6500 | 0.045829
| 7000 | -1.1391
| 7500 | -1.3071
| 8000 | -0.020522
| 8500 | 3.2152
First Pre-Fitler
1= No Prefilter
2= 2" Aluminum Mesh | 2
3= 2" Baffle Impinger
4= 2" Pleated Prefilter | 0 | 12.6083
5= 4" Pleated Prefilter | 500 | 12.0883
6= Pink & White MaxiGrid Panel | 1000 | 12.0795
| 1500 | 12.2785
| 2000 | 12.4389
| 2500 | 12.3715
| 3000 | 11.9438
| 3500 | 11.0805
| 4000 | 9.7631
| 4500 | 8.0304
| 5000 | 5.978
| 5500 | 3.7585
Cell to copy | 6000 | 1.5815
-5.0205 | 6500 | -0.28633
| 7000 | -1.5213
| 7500 | -1.7429
| 8000 | -0.51331
| 8500 | 2.662
Second Pre-Fitler
1= No Prefilter
2= 2" Aluminum Mesh | 5
3= 2" Baffle Impinger
4= 2" Pleated Prefilter | 0 | 12.624
5= Pink & White MaxiGrid Panel | 500 | 12.0566
| 1000 | 11.9837
| 1500 | 12.1018
| 2000 | 12.1647
| 2500 | 11.9829
| 3000 | 11.4242
| 3500 | 10.413
| 4000 | 8.9312
| 4500 | 7.0172
| 5000 | 4.7668
| 5500 | 2.3325
| 6000 | -0.07594
| 6500 | -2.1919
| 7000 | -3.6919
| 7500 | -4.1951
| 8000 | -3.2639
| 8500 | -0.40377
Bag Filter
1= No Bag Filter
2 = 55% Bag Filter | 4
3 = 95% Bag Filter
4 = 95% Oil Mist Bag Filter | 0 | 12.6216
| 500 | 12.0175
| 1000 | 11.8963
| 1500 | 11.9547
| 2000 | 11.9463
| 2500 | 11.6817
| 3000 | 11.0286
| 3500 | 9.9116
| 4000 | 8.3124
| 4500 | 6.2695
| 5000 | 3.8787
| 5500 | 1.2925
| 6000 | -1.2794
| 6500 | -3.5703
| 7000 | -5.2568
| 7500 | -5.958
| 8000 | -5.2364
| 8500 | -2.5973
Afterfilter
1= No After Filter
2=99.97% Hepa (Not Available) | 1
3= 95% Hepa (Not Available)
| 0 | 12.6216
| 500 | 12.0175
| 1000 | 11.8963
| 1500 | 11.9547
| 2000 | 11.9463
| 2500 | 11.6817
| 3000 | 11.0286
| 3500 | 9.9116
| 4000 | 8.3124
| 4500 | 6.2695
| 5000 | 3.8787
| 5500 | 1.2925
| 6000 | -1.2794
| 6500 | -3.5703
| 7000 | -5.2568
| 7500 | -5.958
| 8000 | -5.2364
| 8500 | -2.5973
Entry Loss Factor (per VP)
0.93 |  |  |  |  | # Of Inlets
|  |  |  | 3 Opening Check==> | 3
Inlet posibilities |  | Quantity |  | Quantity |  | Quantity |  | Quantity
3-Open-Intets | 16" | 3 | 14" | 0 | 12" | 0 | 10" | 0
3-16" | Area => | 4.1887 | Area => | 0 | Area => | 0 | Area => | 0
2-16" 1-14"
2-16" 1-12" | 0 | 12.6216
2-16" 1-10" | 500 | 12.0166
1-16" 2-14" | 1000 | 11.893
1-16" 1-14" 1-12" | 1500 | 11.9472
1-16" 1-14" 1-10" | 2000 | 11.933
1-16" 2-12" | 2500 | 11.661
1-16" 1-12" 1-10" | 3000 | 10.9989
1-16" 2-10" | 3500 | 9.8711
3-14" | 4000 | 8.2595
2-14" 1-12" | 4500 | 6.2026
2-14" 1-10" | 5000 | 3.7961
1-14" 2-12" | 5500 | 1.1925
1-14" 1-12" 1-10" | 6000 | -1.3983
1-14" 2-10" | 6500 | -3.71
3-12" | 7000 | -5.4187
2-12" 1-10" | 7500 | -6.1439
1-12" 2-10" | 8000 | -5.4478
3-10" | 8500 | -2.836
2-Open-Intets
2-16"
1-16" 1-14"
1-16" 1-12"
1-16" 1-10"
2-14"
1-14" 1-12"
1-14" 1-10"
2-12"
1-12" 1-10"
2-10"
1-Open-Intet
1-16"
1-14"
1-12"
1-10"